RE: IEC 61850 PIXIT Template v0.2draft.doc  Print |  New Window Full Message Bruce Muschlitz to Schimmel, Richard, schwarz, testing, Pastors, Christof, TAN Jian-Cheng, dean, Phil Young, Marco C. Janssen, Shengwu.Zeng, clemens.hoga - Jun 19More Details From:  Bruce Muschlitz <bruce@enernex.com>Hide Add to: Blog, To Do, Calendar To:  Schimmel, Richard <Richard.Schimmel@kema.com>    schwarz@scc-online.de    testing@ucausersgroup.org    Pastors, Christof <christof.pastors@siemens.com>    TAN Jian-Cheng <Jian-Cheng.TAN@kinectrics.com>    dean@rtds.com    Phil Young <pyoung@TriangleMicroWorks.com>    Marco C. Janssen <marco@enernex.com>    Shengwu.Zeng@utinnovation.com    clemens.hoga@siemens.comCc:Bcc:Date:Thu, 19 Jun 2008 7:10 am

Richard and Karlheinz:

There are two independent parts of the problem: publisher side and subscriber

side.

On the publisher side, the combination of retransmit curve and TATL curve define

the minimum number of lost GSE packets which will cause subscriber to generate

an "association lost" condition. This is a necessary, but not sufficient,

condition for the subscribers to take action. The information needed to

calculate this "dropped GSE count" should be in the PIXIT.

On the subscriber side, there may be any number of algorithms to cause a delay

from "association lost" to "action needs to be taken" such as remembering the

last TATL, recording the last retransmission interval, using a fixed number of

seconds (including zero), etc. The "delay" algorithm must be exposed in the

PIXIT in order to determine whether a publisher and subscriber can inter-operate

under dropped-packet conditions.

Consider the case where a (not configurable) publisher sets the TATL at 2200

mSec and transmits every 2000 mSec connected to a (not configurable) subscriber

which immediately goes into backup-protection mode upon "association lost". We

now have a "barely inter-operable system" which probably does not operate as

intended. The only solution would be replacement of either the publisher or

subscriber with another product (or firmware revision). System integrators

certainly would not want to find this out at the end of commissioning stage.

There is at least one relay manufacturer which does operate in this manner. I

think that if we explained to users that a single lost packet might cause

unexpected system actions, there might be some concern. Hiding this fact by not

publishing details is not the best solution.

Also note that 61850-8-1 clause 18.1.2.5 Figure 9, note 1 "It is suggested that

the retransmission timer be less than (actually half) of the [TATL] parameter."

which supports my assertion that part 8-1 intended that subscribers can take

immediate action upon TATL timeout.

I am not trying to restrict GSE implementations, I am just trying to increase

the probability of interoperability and reduce the chance that protection

schemes need to be re-designed based upon individual manufacturer

interpretations of 61850.

I have other GSE interoperability issues such as publishers which do not adjust

the TATL based upon the retransmission time, but those issue can wait until 8-1

CD/CDV.

To summarize, I think we need only two more PIXIT entries:

- publishers need to specify : minimum number of dropped GSE packets before

subscribers can declare association lost. This value is easily testable by

recording GSE reception time intervals against TATL for the entire

retransmission cycle (to steady state)

- subscribers need to specify : action taken upon GSE association lost. This is

most easily testable at steady state where you can unplug the publisher and view

the subscriber for the declared actions

Regards ... Bruce Muschlitz