Test procedures for GOOSE performance according to IEC 61850-5 and IEC 61850-10 Version 1.2

On request of UCA International Users Group

Baden, July 2, 2012

| author : Richard Schimmel Stephan Gerspach |  | reviewed : UCAIUG testsub |  |
| --- | --- | --- | --- |
| B 27 pages 2 annexes | SG | approved : UCAIUG testsub |  |

CONTENTS

page

1	Introduction	5

1.1	Test methodology	6

1.2	Test scope	8

1.3	Glossary	9

1.4	Identifications	10

2	References	11

2.1	Normative	11

2.2	Other	12

3	Test environment	13

4	GOOSE performance testing	14

4.1	Message definitions	14

4.1.1	Published GOOSE used for ping-pong	14

4.1.2	Subscribed GOOSE used for ping-pong	15

4.1.3	Time correlated Subscribed GOOSE not used for ping-pong	16

4.1.4	Not subscribed GOOSE	16

4.1.5	Other communication tasks	17

4.2	Test cases	17

4.3	Test passed criteria	18

4.4	Test results	20

4.5	Detailed test procedure	21

Annex A 	Pixit Template For Goose Performance Test

Annex B 	Template For Goose Performance Test Certificate

# Introduction

The scope of the test is to benchmark the GOOSE performance of the DUT against the performance classes as defined in IEC 61850-5. IEC 61850-5 clause 13 states:

13.7.1.1 Type 1A “Trip” : The trip is the most important fast message in the substation. Therefore, this message has more demanding requirements compared to all other fast messages. The same performance may be requested for interlocking, intertrips and logic discrimination between protection functions.

- For Performance Class P1, the total transmission time shall be in the order of half a cycle. Therefore, 10 ms is defined.

- For Performance Class P2/3, the total transmission time shall be below the order of a quarter of a cycle. Therefore, 3 ms is defined.

IEC 61850-5 defines the transmission time as follows

Figure 1: Transmission time definition IEC 61850-5

## Test methodology

Measuring the transmission time as defined in IEC 61850-5 is not possible without special access to the internal data of the device. To enable "black-box" testing a test lab needs a different test methodology referred to as the "GOOSE ping-pong" method. This method is already in use for GOOSE conformance testing.

Figure 2:	Measure round trip time using GOOSE ping-pong method

The GOOSE ping-pong method focuses on the round trip time as defined in figure 2. The round trip time is the time interval between the arrival of a subscribed GOOSE message and the departure of the published GOOSE message:  troundtrip = (ty – tx).

The relation between the transfer time and roundtrip time is as follows:

# ttransfer 				= ta + tb + tc

# troundtrip 	= (ty – tx)	= tc* + tapplication + ta

When PD1 and PD2 are the same we assume that the GOOSE publish and subscribe  communication processing times are the same in figure 1 and 2. In that case we can combine these equations into:

- ttransfer = troundtrip – tapplication + tb

We assume the network delay for a single Ethernet switch to be minimal (< 0.1ms).  Then we get

- ttransfer = troundtrip – tapplication

ta 			= GOOSE publish communication processing

tb 			= network delay of one GOOSE message

tc 			= GOOSE subscribe communication processing

tapplication 	= application time

The application time typically is the sum of the scan cycle wait time and the actual application logic processing time. On a scan cycle of for example 4 ms the average scan cycle wait time is about 2 ms (50% of scan cycle). The difference between the maximum and the minimum of the measured roundtrip times will be close to the scan cycle. These metrics can be used to perform a plausibility check on the documented figures in the PIXIT document.

# According to IEC 61850-10 a test system shall measure latency time by generating a sequence of physical/virtual input triggers to the IED and measuring the time delay to the corresponding message generated by the IED. The mean latency time and the standard deviation shall be computed across the responses to 1000 input triggers.

# Transmission schema for GOOSE to be published for Ping Pong:

# To facilitate measuring the roundtrip time, as close to the worst case as possible, the input triggers related to the GOOSE to be published for Ping Pong has to be randomised.
The transmission schema including randomisation looks as follow:

# tpublisched = tapplication *2,5 +/- 50% * tapplication = Range for randomised Ping-Pong

In case the DUT has an event driven method (no scan cycle), tapplication of 50 ms shall be used to calculate the transmission schema.

# Example:

# tapplication = 100 ms

# tpublished = tapplication *2,5 +/- 50% * tapplication = 200ms – 300ms = Range for randomised Ping-Pong

# To secure the retransmission pattern, minimum value of tpublisched shall not be below 100ms.

# In case the DUT has an tapplication  ≤ 50 ms, for calculation of the tpublisched time tapplication shall be set to 50 ms.
By applying this rule the retransmission pattern of GOOSE mechanism is secured,by an  minimum value of tpublisched  oft 100ms.

## Test scope

The following items may have an impact on the GOOSE performance:

- Size of the published/subscribed GOOSE message (number of data set elements)

- Type of data set elements

- Which element of the data set is used

- Use of Functionally Constrained Data (FCD) or Functional Constrained Data Attributes (FCDA) in the dataset

- Number of subscribed GOOSE messages

- Time correlation of subscribed GOOSE messages state changes

- Number of non-subscribed GOOSE messages on the network

- Other communication tasks like MMS reporting, file transfer and/or Sampled Values when supported

This test procedure is intended as a benchmark for comparing relative performance of different IEDs. It defines standardized tests aimed at mimicking typical workload conditions. It does not test device performance under worst case load, worst case network conditions, or in a specific system application. Please refer to detailed vendor specifications for full description of the device capabilities, behaviour and limitations.

## Glossary

BRCB		Buffered Report Control Block

DUT		Device Under Test

DP			Double Point Information

GoCB		GOOSE Control Block

GOOSE	Generic Object Oriented System Event

ICD		IED configuration description in SCL-format

IED 		Intelligent Electronic Device

FCD		Functionally Constrainted Data

FCDA		Functionally Constrainted Data Attributes

PICS		Protocol Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

MAC		Media Access Control

ms			milliseconds

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

UCAIUG	UCA International Users Group

URCB		Unbuffered Report Control Block

VLAN		Virtual Local Area Network

## Identifications

The following table gives the exact identification of tested equipment and test environment used for this performance test.

| DUT | 670 series 1.2.3.5 Software Version: 1.5.0.35 Hardware Version: 1MRK002812-XB Serial Number: T0724122 Performance class: P1 |
| --- | --- |
| MANUFACTURER | ABB AB SA Products S_721 59 Västeras Sweden |
| PICS | 1MRG000835 ABB 670 series version 1.2 IEC61850 PICS |
| PIXIT | 670 series GOOSE Performance PIXIT |
| ICD or SCD | Omicron SCD von IET600 |
| TEST INITIATOR | ABB |
| TEST FACILITY | System Verification & Validation Center, ABB Switzerland, Bruggerstrasse 72, 5400 Baden, Switzerland |
| TEST ENGINEER | Stephan Gerspach, Stephan.Gerspach@ch.abb.com |
| TEST SESSION | 2011-09-27 Baden, Switzerland |
| ANALYSER | National Instruments, Gigastore, version 14.1 ABB, ITT, version 1.6.0.1 |
| GOOSE PUBLISHER | ABB, ITT, version 1.2.8 Omicron Test Univers 2.40 SR1 |
| CLIENT | ABB, Vendor |
| TIME MASTER | Meinberg LanTime, GPS Clock |
| ETHERNET SWITCH | RuggedCOM RSG2100, Version 3.9.2 |

The DUT shall be a regular production model. The only tuning that is allowed is ‘off-the-shelf’ configuration to minimize the application logic.

# References

## Normative

The tests defined in this document are based on the following IEC 61850 documents.

IEC/TR 61850-1, Communication networks and systems in substations – Part 1: Introduction and overview; First edition 2003-04

IEC/TS 61850-2, Communication networks and systems in substations – Part 2: Glossary; First edition 2003-08

IEC 61850-3, Communication networks and systems in substations – Part 3: General requirements; First edition 2003-01.

IEC 61850-4, Communication networks and systems in substations – Part 4: System and project management; First edition 2003-01

IEC 61850-5, Communication networks and systems in substations – Part 5: Communication requirements for functions and device models; First edition 2003-07

IEC 61850-6, Communication networks and systems in substations – Part 6: Substation Automation System configuration language; First edition 2004-03

IEC 61850-7-1, Communication networks and systems in substations – Part 7-1: Basic communication structure for substation and feeder equipment – Principles and models; First edition 2003-07

IEC 61850-7-2, Communication networks and systems in substations – Part 7-2: Basic communication structure for substation and feeder equipment – Abstract communication service interface (ACSI); First edition 2003-05

IEC 61850-7-3, Communication networks and systems in substations – Part 7-3: Basic communication structure for substation and feeder equipment – Common data classes and attributes; First edition 2003-05

IEC 61850-7-4, Communication networks and systems in substations – Part 7-4: Basic communication structure for substation and feeder equipment – Compatible logical node and data object addressing; First edition 2003-05

IEC 61850-8-1, Communication networks and systems in substations – Part 8-1: Specific communication service mapping (SCSM) – Mappings to MMS (ISO/IEC 9506-1 and ISO/IEC 9506-2) and to ISO/IEC 8802-3; First edition 2004-05

IEC 61850-10, Communication networks and systems in substations – Part 10: Conformance testing; First edition 2005-05

## Other

IS 9646 – OSI – Conformance testing methodology and framework

UCA International User Group: Quality Assurance Program

UCA International User Group: Accreditation and Recognition Program for IEC 61850 Device Testing

http://www.tissues.iec61850.com

# Test environment

The test environment consists of the following components:

Figure 3: The test environment

The analyzer compares the published and the subscribed GOOSE messages from the DUT.

The MMS client is used to initiate Client/Server (MMS) communication during the test

The DUT shall not be reconfigured during the performance test. The test procedures are designed in such a way that the DUT doesn't need to be reconfigured during the performance test.

# GOOSE performance testing

## Message definitions

The general message requirements are:

- Each GOOSE has unique multicast destination MAC address

- Each GOOSE has VLAN priority = 4 and VLAN ID = 0

- Each GOOSE has APPID = 0x3001

- Each GOOSE has Test = FALSE, NdsCom = FALSE

- The GOOSE datasets contain functionally constrained data attributes (FCDA)

- The BRCB or URCB datasets contain functionally constrained data (FCD)

### Published GOOSE used for ping-pong

The DUT will publish the following GOOSE:

Dataset					normal dataset = 4 Boolean data values and 4 qualities

Structure normal dataset:

(bool1, q1, bool2, q2, bool3, q3, bool4, q4)

large dataset =20 Boolean values with qualities and 20 DP values with qualities.

Structure large dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema	 Will be published as soon as possible then the Ping Goose was subscribed.

GoCB name				GPFPPpongNormal, 			GPFPPpongLarge

Dataset name	GPFPPpongNormal 			GPFPPpongLarge

Destination MAC			0x01 0C CD 01 00 01, 		0x01 0C CD 01 00 02

### Subscribed GOOSE used for ping-pong

The DUT will subscribe to the following GOOSE:

Dataset					normal dataset = 4 Boolean data values and 4 qualities

Structure normal dataset:

(bool1, q1, bool2, q2, bool3, q3, bool4, q4)

large dataset = 20 Boolean values with qualities and 20 DP values with qualities.

Structure large dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema	To be calculated based on scan cycle time of DUT according to 1.1 Test methodology..
Maximum 10, minimum 4 State changes per second

Retransmission at 4 and 32 ms (or more)

GoCB name				GPFPPpingNormal, 			GPFPPpingLarge

Dataset name				GPFPPpingNormal 			GPFPPpingLarge

Destination MAC			0x01 0C CD 01 00 03			0x01 0C CD 01 00 04

### Time correlated Subscribed GOOSE not used for ping-pong

The DUT will also subscribe to the following GOOSE:

Dataset	large dataset = 20 Boolean values with qualities and 20 DP values with qualities.

Structure of dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema		5 subscribed GOOSE control blocks

Retransmission at 4, 32 and 256 ms (or more)

5 subscribed GOOSE each having one state change of the 5th data value element at approximately -4.0, -2.0, 0.0, 2.0 and 4.0 ms before and after the subscribed GOOSE state change used for ping-pong.

Gocb name	GPFsubscribed1.. 5

Dataset name	GPFsubscribed1..5

Destination MAC	0x01 0C CD 01 00 05 to 0x01 0C CD 01 00 09

### Not subscribed GOOSE

Dataset	large dataset6 = 20 Boolean values with qualities and 20 DP values with qualities.

Structure of dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema	100 GOOSE control blocks each with 1 state change per second (about every 10 ms) and 2 retransmissions per second (at 32 and 256 ms or more). The total number of these GOOSE messages will be at least 300 messages per second.

Gocb name8				GPFnotSubscribed001..100

Dataset name				GPFnotSubscribed001..100

Destination MAC	0x01 0C CD 01 11 01    to    0x01 0C CD 01 11 64

### Other communication tasks

In case the DUT supports reporting one client shall be connected to the DUT during all test cases. The client enables two BRCBs or when buffered reporting is not supported two URCBs with same data values (as FCD) as the normal and large dataset in the published GOOSE. The report control blocks shall be configured to send reports on data change and quality change with all supported optional fields.

## Test cases

The following table gives an overview of the test cases.

| Test ID | Subscribe (ping) | Publish (pong) | Time correlated Subscribed GOOSE not used for ping-pong | Not subscribed |
| --- | --- | --- | --- | --- |
| Gpf1 | Normal | Normal | No | No |
| Gpf2 | LARGE | LARGE | No | No |
| Gpf3 | Normal | Normal | YES | No |
| Gpf4 | LARGE | LARGE | YES | No |
| Gpf5 | Normal | Normal | No | YES |
| Gpf6 | LARGE | LARGE | No | YES |
| Gpf7 | Normal | Normal | YES | YES |
| Gpf8 | LARGE | LARGE | YES | YES |

Note: "No" means that the GOOSE publisher will not publish GOOSE message, because they are not relevant for this test case.

The DUT shall not be reconfigured during the tests.

GOOSE publisher will not publishing GOOSE related to the LARGE GCB during NORMAL tests (Gpf1,3,5,7) and not publishing GOOSE related to NORMAL GCB during LARGE tests (Gpf2,4,6,8). DUT will publishing in all test cases GOOSE related to LARGE and Normal GCB.

## Test passed criteria

For performance class P1 the transmission limit is defined as 10 ms and 3 ms for P2/P3. According to IEC 61850-10 clause 7.2.1 the performance results are the average and standard deviation over 1000 input triggers and that the sum of the measured output and input latency shall be less than or equal to 80 % of the total transmission (because 20% is reserved for network latency).

In clause 1.1 we determined:  ttransfer = troundtrip – tapplication. The application time typically is the sum of the internal scan cycle wait time and the actual logic processing time. To represent  the worst case transfer time we set the actual logic processing time to zero (this means that the logic processing time is considered as part of the transfer time). As a result we get:

- Average application time 		=   50% of scan cycle

- Maximum application time 	= 100% of scan cycle

- Minimum application time 	=     0% of scan cycle

Now the transfer time can be calculated as follows:

- Average:	ttransfer.avg = troundtrip.avg – tapplication.avg 	= troundtrip.avg – scancycle/2

- Maximum:	ttransfer.max = troundtrip.max – tapplication.max 	= troundtrip.max – scancycle

- Minimum:	ttransfer.min = troundtrip.min – tapplication.min 	= troundtrip.min

Note: it is possible that the calculated maximum transfer time is less than the calculated minimum transfer time.

Plausibility checks:

- Documented scan cycle ≤ Measured scan cycle = troundtrip.max – troundtrip.min

- Documented scan cycle ≤ Measured standard deviation * 3.46   (for uniform distribution)

In case the measured scan cycle is more than 1 ms below the documented scan cycle, the documented scan cycle shall be adjusted by the vendor.

The adjusted scan cycle time has to be taken for the final performance calculation

In case the DUT has an event driven method (no scan cycle) the scan cycle for the calculations is set to 0.0 ms.

To pass the performance test the criteria are:

- Gpf1 to Gpf6 test are passed when the calculated average, maximum and minimum transfer times are less than 80% of the applicable performance class limit (IEC 61850-10 clause 7.2.1 Note 1):

  - Performance class P1; 		ttransfer < 8.0 ms

  - Performance class P2/P3; 	ttransfer < 2.4 ms

- Gpf7 and Gpf8 test is passed when the average, maximum and minimum calculated transfer times are less than 100% of the performance class limit:

  - Performance class P1; 		ttransfer <10.0 ms

  - Performance class P2/P3; 	ttransfer <  3.0 ms

The PIXIT document shall specify the GOOSE performance class and application logic scan cycle(s).

The DUT has passed the GOOSE performance test when all test cases are passed.

## Test results

Documented scan cycle 	= 100.0 ms

Measured scan cycle 		= 101.10 ms (average over all 8 goose performance test cases)

Performance class 		= P1

| Test ID | Minimum | Maximum | Average | Verdict |
| --- | --- | --- | --- | --- |
|  |  | Round-trip | Transfer | Round-trip | Transfer | Stddev |  |
| Gpf1 |  |  |  |  |  |  | Passed |
| Gpf2 |  |  |  |  |  |  | Passed |
| Gpf3 |  |  |  |  |  |  | Passed |
| Gpf4 |  |  |  |  |  |  | Passed |
| Gpf5 |  |  |  |  |  |  | Passed |
| Gpf6 |  |  |  |  |  |  | Passed |
| Gpf7 |  |  |  |  |  |  | Passed |
| Gpf8 |  |  |  |  |  |  | Passed |

## Detailed test procedure

| Gpf1 | GOOSE performance tests Based on Normal Dataset | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf1 = with normal Subscribe (ping) |
| Comment Gpf1 transfertimemax =5,99ms |

| Gpf2 | GOOSE performance tests Based on Large Dataset | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf2 = with large Subscribe (ping) |
| Comment Gpf2 transfertimemax = 2,50 ms Any deviation to Large Dataset structure as defined? No. |

| Gpf3 | GOOSE performance tests Based on Normal Dataset and time correlated Subscribed GOOSE | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf3 = with normal Subscribe (ping) & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf3 transfertimemax = 4,0 ms |

| Gpf4 | GOOSE performance tests Based on Large Dataset and time correlated Subscribed GOOSE | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf4 = with large Subscribe (ping) & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf4 transfertimemax = 3,39 ms Any deviation to Large Dataset structure as defined? No. |

| Gpf5 | GOOSE performance tests Based on Normal Dataset and not Subscribed GOOSE | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf5 = with normal Subscribe (ping) & not subscribed GOOSE |
| Comment Gpf5 transfertimemax = 6,00 ms |

| Gpf6 | GOOSE performance tests Based on Large Dataset and not Subscribed GOOSE | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf6 = with large Subscribe (ping) & not subscribed GOOSE |
| Comment Gpf6 transfertimemax = 2,40 ms Any deviation to Large Dataset structure as defined? No. |

| Gpf7 | GOOSE performance tests Based on Normal Dataset , time correlated Subscribed GOOSE and not Subscribed GOOSE | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf7 = with normal Subscribe (ping) & not subscribed GOOSE & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf7 transfertimemax = 3,70 ms |

| Gpf8 | GOOSE performance tests Based on Normal Dataset , time correlated Subscribed GOOSE and not Subscribed GOOSE | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. MMS Client associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE publisher as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf8 = with large Subscribe (ping) & not subscribed GOOSE & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf8 transfertimemax = 3,79 ms Any deviation to Large Dataset structure as defined? No. |

# Footnotes

The APPID shall be the same for all GOOSE Messages during the Tests but the value it self can be different as defined above in case there are some limitation related to the DUT

In case the DUT does not support 20 Boolean or 20 DP, or the DUT has some limitations regarding dataset size, the LARGE Dataset shall contain at least 40 values and 40 qualities or the maximum number of dataset entries that is possible according to the description in PIXIT.

By using the names defined in the test procedures the analyzing of the capture files would be much easier, but the names have no impact to the performance. So alternative names are allowed

In case the DUT does not support 20 Boolean or 20 DP, or the DUT has some limitations regarding dataset size, the LARGE Dataset shall contain at least 40 values and 40 qualities or the maximum number of dataset entries that is possible according to the description in PIXIT.

By using the names defined in the test procedures the analyzing of the capture files would be much easier, but the names have no impact to the performance. So alternative names are allowed.

In case the DUT does not support 20 Boolean or 20 DP, or the DUT has some limitations regarding dataset size, the LARGE Dataset shall contain at least 40 values and 40 qualities or the maximum number of dataset entries that is possible according to the description in PIXIT.

Timing accuracy of state changes in relation to subscribed GOOSE sate changes shall be ±1ms!

By using the names defined in the test procedures the analyzing of the capture files would be much easier, but the names have no impact to the performance. So alternative names are allowed.

In case trigger option “quality change” is not supported data change is sufficient.

http://en.wikipedia.org/wiki/Uniform_distribution_(continuous)

# Text boxes

This document may be distributed to UCA international users group members only.

Communication processor

Application Logic to

copy value

Physical device PD1

troundtrip

tx

ty

subscribed GOOSE messages

published GOOSE messages

tc

tapplication

ta

GOOSE Publisher

High Performance Analyzer

Ethernet Switch

MMS Client

Device Under Test

Time Master