30900601-Consulting 09-version0.2b

Test procedures for GOOSE performance according to IEC 61850-5 and IEC 61850-10 Version 0.2b (DRAFT With comments from STRI Independent IEC 61850 Interoperability Laboratory)

On request of UCAIUG

January 19, 2010

Authors Richard Schimmel and Tao Xu

KEMA Consulting

Comments entered by Nicholas Etherden, STRI, Sweden

0

| author : Richard Schimmel |  | reviewed : Bas Mulder |  |
| --- | --- | --- | --- |
| B 22 pages 2 annexes | RS | approved : Willem strabbing |  |

CONTENTS

page

1	Introduction	4

1.1	Test methodology	4

1.2	Test scope	6

1.3	Glossary	6

1.4	Identifications	6

2	Test environment	7

3	GOOSE performance testing	9

3.1	Message definitions	9

3.1.1	Published GOOSE used for ping-pong	9

3.1.2	Subscribed GOOSE used for ping-pong	9

3.1.3	Subscribed GOOSE not used for ping-pong	10

3.1.4	Not subscribed GOOSE	10

3.1.5	Other communication tasks	10

3.2	Test cases	11

3.3	Test passed criteria	11

3.4	Detailed test procedure	13

# Introduction

The scope of the test is to verify and measure the GOOSE performance against the performance classes as defined in IEC 61850-5. IEC 61850-5 clause 13 states:

13.7.1.1 Type 1A “Trip” : The trip is the most important fast message in the substation. Therefore, this message has more demanding requirements compared to all other fast messages. The same performance may be requested for interlocking, intertrips and logic discrimination between protection functions.

- For Performance Class P1, the total transmission time shall be in the order of half a cycle. Therefore, 10 ms is defined.

- For Performance Class P2/3, the total transmission time shall be below the order of a quarter of a cycle. Therefore, 3 ms is defined.

IEC 61850-5 defines the transmission time as follows

Figure 1: Transmission time definition IEC 61850-5

## Test methodology

To measure the transmission time as defined in IEC 61850-5 is not possible without special access to the internal data of the device. To enable "black-box" testing we need a different test methodology. Therefore we will use the "GOOSE ping-pong" method. This method is already in use for GOOSE conformance testing.

Figure 2:	Measure round trip time using GOOSE ping-pong method

The GOOSE ping-pong method focuses on the round trip time as defined in figure 2. The round trip time is the time interval between the arrival of a subscribed GOOSE message and the departure of the published GOOSE message:  troundtrip = (ty – tx).

The relation between the transfer time and roundtrip time is as follows:

# ttransfer 				= ta + tb + tc

# troundtrip 	= (ty – tx)	= tc + tapplication + ta

When we combine these equations we get:

- ttransfer = troundtrip – tapplication + tb

We assume the network delay for a single ethernet switch to be minimal (< 0.1msec).  Then we get

- ttransfer = troundtrip – tapplication

ta 			= GOOSE publish communication processing

tb 			= network delay of one GOOSE message

tc 			= GOOSE subscribe communication processing

tapplication 	= application logic processing

The application logic typically depends on the internal scan cycle. On a internal scan cycle of for example 4 miliseconds the average application time is about 2 milliseconds (50% of scan cycle). The measured maximum – minimum roundtrip times will be close to the scan cycle. These metrics can be used to perform a plausibility check on the documented figures in the PICS or PIXIT documents.

# According to IEC 61850-10 a test system shall measure latency time by generating a sequence of physical/virtual input triggers to the IED and measuring the time delay to the corresponding message generated by the IED. The mean latency time and the standard deviation shall be computed across the responses to 1000 input triggers. The vendor shall define and document the amount of the latency time which is due to estimated output processing time (note: this is about half of the roundtrip time).

## Test scope

The following items may have an impact on the GOOSE performance:

- Size of the published/subscribed GOOSE message (number of data set elements)

- Type of data set elements

- Which element of the data set is used

- Use of Functionally Constrained Data or Functional Constrained Data Attributes in dataset

- Number of subscribed GOOSE messages

- Time correlation of subscribed GOOSE messages

- Number of non-subscribed GOOSE messages on the network

- Load of CPU processing GOOSE

- Other communication tasks like MMS reporting, file transfer and/or Sampled Values when supported

## Glossary

DUT		Device Under Test

GOOSE	Generic Object Oriented System-wide EventICD		IED configuration description in SCL-format

IED 		Intelligent Electronic Device

MICS		Model Implementation Conformance Statement

PICS		Protocol Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

UCAIUG	UCA International Users Group

## Identifications

The following table gives the exact identification of tested equipment and test environment used for this performance test.

| DUT | <identification and short name of the device under test> <hardware and software version> Performance class: P1 or P2/P3 Documented GOOSE output processing latency = x.y msec Documented GOOSE application scan cycle = x.y msec or not applicable |
| --- | --- |
| MANUFACTURER | <name, location of the manufacturer of the DUT> |
| PICS | <complete reference description of the PICS> |
| MICS | <complete reference description of the MICS> |
| TICS | <complete reference description of the TICS> |
| PIXIT | <complete reference description of the PIXIT> |
| ICD or SCD | <complete reference description of the SCL configuration file> |
| TEST INITIATOR | MANUFACTURER, USER, SYSTEM INTEGRATOR |
| TEST FACILITY | <name and address of test facility> |
| TEST ENGINEER | <name and e-mail address of test engineer> |
| TEST SESSION | <date and location of the test session> |
| ANALYSER | <name and type analyzer(s), version X.Y> |
| GOOSE SIMULATOR | <name and type GOOSE simulator> |
| SV SIMULATOR | <name and type SV simulator> |
| CLIENT SIMULATOR | <name and type client simulator> |
| TIME MASTER | <name and type of time master> |

# Test environment

The test environment consists of the following components:

Figure 3: The test environment

The analyzer compares the published and the subscribed GOOSE messages from the DUT.

The DUT shall not be reconfigured during the performance test. The test procedures shall be designed in such a way that the DUT doesn't need to be reconfigured during the performance test.

# GOOSE performance testing

## Message definitions

The general message requirements are:

- Each GOOSE has unique multicast destination MAC address

- Each GOOSE has VLAN priority 4 and the same VLAN ID

- Each GOOSE has Test = FALSE, ConfRev = 1, NdsCom = FALSE

- GOOSE dataset with data attributes (not data objects)

### Published GOOSE used for ping-pong

The DUT will publish the following GOOSE

GOOSE format			normal dataset = 4 Boolean data values and 4 qualities

large dataset = 20 Double Point data values, 20 Boolean Data values and 40 qualities

Transmission schema		Given by subscribed GOOSE, retransmission scheme as specified in the DUT documentation

GooseID					GPFPP_pong_normal, GPFPP_pong_large

GoCB name				GPFPPpongNormal, GPFPPpongLarge

Destination MAC			0x01 0C CD 01 00 01 and 00 02

### Subscribed GOOSE used for ping-pong

The DUT will subscribe to the following GOOSE

GOOSE format			normal dataset = 4 Boolean data values and 4 qualities

large dataset = 20 Double Point data values, 20 Boolean Data values and 40 qualities

Transmission schema	4 state changes of the 3rd data value element per second (each 250 milliseconds)

Retransmission at 4 and 32 msec (or more)

GooseID					GPFPP_ping_normal, GPFPP_ping_large

gocbRef	GPFPPpingNormalLD0/LLN0$GO$GPFPPpingNormal GPFPPpingLargeLD0/LLN0$GO$GPFPPpingLarge

DatSet name	GPFPPpingNormalLD0/LLN0$GPFPPpingNormal GPFPPpingLargeLD0/LLN0$GPFPPpingLarge

Destination MAC			0x01 0C CD 01 00 03 and 00 04

### Subscribed GOOSE not used for ping-pong

GOOSE format			large dataset = 20 Double Point data values, 20 Boolean data values and 40 qualities

Transmission schema		5 subscribed GOOSE control blocks

Retransmission at 4, 32 and 256 msec (or more)

Time correlated	5 subscribed GOOSE have a statechange of the 5th data value element at -4, -2, 0, 2 and 4 msec after the subscribed GOOSE state change used for ping-pong

Not time correlated	5 subscribed GOOSE have statechange of the 5th data value element at about 50-150 msec after the state change used for ping-pong

GooseID					GPF_subscribed1..5

gocbRef	GPFsubscribed1..5LD0/LLN0$GO$GPFsubscribed1..5

DatSet name				GPFsubscribed1..5LD0/LLN0$GPFsubscribed1..5

Destination MAC			0x01 0C CD 01 00 05 to 00 09

### Other communication tasks

Report:	One client enables one URCB or BRCB with same data values (as objects) as the published GOOSE; 	The report will be send on data change with integrity 1 second and all optional fields

Sampled Values (optional):One merging unit is sending valid sampled value messages subscribed by the device

During normal operation a client is connected to the device. During the test a client is connected for all test cases. In case the DUT supports Sampled Values also valid sampled values can optionally be provided during all test cases.

## Test cases

The following table gives an overview of the test cases.

| Test ID | Publish (pong) | Subscribe (ping) | Subscribe Not used for ping-pong |  |
| --- | --- | --- | --- | --- |
|  |  |  |  | Time correlated |  |
| Gpf1 | Normal | Normal |  | No |  |
| Gpf2 | LARGE | LARGE |  | No |  |
| Gpf4 | Normal | Normal |  | YES |  |
| Gpf6 | LARGE | LARGE |  | YES |  |

| Test ID | Publish (pong) | Subscribe (ping) | Subscribe Not used for ping-pong |
| --- | --- | --- | --- |
|  |  |  | Time correlated |
| Gpf1 | Normal | Normal | No |
| Gpf2 | LARGE | LARGE | No |
| Gpf4 | Normal | Normal | YES |
| Gpf6 | LARGE | LARGE | YES |

Note: "No" means that the GOOSE simulator will retransmit each GOOSE message without state change each second to prevent GOOSE subscribe errors.

## Test passed criteria

For performance class P1 the transmission limit is defined as 10 msec and 3 msec for P2/P3. According to IEC 61850-10 clause 7.2.1 the performance results are the average and standard deviation over 1000 input triggers and that the measured output (input) latency shall be less than or equal to 40 % of the total transmission (because 20% is reserved for network latency).

Based on the following assumptions:

- AVG application time = 50% of scan cycle

- MAX application time = 100% of scan cycle

- MIN application time = 0% of scan cycle

- The variation in receive/transmit processing is much less than the scan cycle

The transfer time can be calculated as follows:

1) 	Average:	ttransfer.avg = troundtrip.avg – tapplication.avg 	= troundtrip.avg – scancycle/2

2) 	Maximum:	ttransfer.max = troundtrip.max – tapplication.max 	= troundtrip.max – scancycle

3) 	Minimum:	ttransfer.min = troundtrip.min – tapplication.min	= troundtrip.min

Plausibility checks:

- scan cycle ≥ troundtrip.max – troundtrip.min

- scan cycle ≥ standard deviation * 3.46   (for even distribution)

In case the measured scan cycle is more then the documented scan cycle, the documented scan cycle shall be adjusted. In case the DUT has an event driven method (no scan cycle) the scan cycle for the calculations is set to 0.0 ms.

To pass the performance test the criteria are:

- Gpf1 to Gpf5 test are passed when the avarage, maximum and minimum calculated transfer times are less than 80% of the applicable performance class limit (IEC 61850-10 clause 7.2.1 Note 1):

  - Performance class P1; 		ttransfer <8 msec

  - Performance class P2/P3; 	ttransfer <2.4 msec

- Gpf6 test is passed when the avarage, maximum and minimum calculated transfer times are less than 100% of the performance class limit:

  - Performance class P1; 		ttransfer <10 msec

  - Performance class P2/P3; 	ttransfer <  3 msec

The PICS or PIXIT document shall specify the GOOSE performance class and application logic scan cycle(s).

The DUT has passed the GOOSE performance test when all test cases are passed.

Detailed test procedure

| Gpf | GOOSE performance tests | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 5. The ping-pong is working 8. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. 3. Start SV simulator when included in test 4. Start high performance analyzer capture 5. Start GOOSE simulator as indicated below 6. Wait for 1000 Subscribe (ping/pong) state changes 7. Stop and save the analyzer capture 8. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum and standard deviation Gpf1 = with normal Subscribe (ping) Gpf2 = with large Subscribe (ping) Gpf4 = with normal Subscribe (ping) AND Subscribe not used for ping-pong time correlated Gpf6 = with large Subscribe (ping) AND Subscribe not used for ping-pong time correlated |
| Comment The measured roundtrip times are: TEST AVERAGE MIN MAX STDEV Gpf1 .. .. .. .. Gpf2 .. .. .. .. Gpf4 .. .. .. .. Gpf6 .. .. .. .. |

# Comments

I have measured difference of almost 20 ms on subscribing to fixed (large) structured GOOSE instead of unstructured (somewhat smaller) GOOSE

File transfer loads the IED long enough to shoot a GOOSE at it during the processing. It is not quite so easy to strike the window during which reports are being processed…

What is normal? This is 100% dependent on application!

“Normal” traffic will be done differently by each test institute, meaning results from different test labs may differ (which doesn’t create confidence among end-users).

Is this one group of four currents and four voltages?

Members of WG 10:  Shall we attempt to get rid of this for the FDIS of Part 10 Ed 2.0? Statement is simply wrong for anything more than a 1 Mbit/s network, Latency is more like 2 ‰ than 20 % in reported measurements...

In practice this means a P2/P3 IED must run GOOSE either event driven or on a cyclicality of 1 or 1,2 ms. A tough but reasonable expectation…

# Text boxes

KEMA Nederland B.V.  Utrechtseweg 310, 6812 AR Arnhem  P.O. Box 9035, 6800 ET Arnhem  The Netherlands

T +31 26 3 56 91 11  F +31 26 3 89 24 77  contact@kema.com  www.kema.com  Registered Arnhem 09080262

Copyright © KEMA Nederland B.V., Arnhem, the Netherlands. All rights reserved.

This document  may be distributed to UCA international users group members only.

KEMA Nederland B.V. and/or its associated companies disclaim liability for any direct, indirect, consequential or incidental damages that may result from the use of the information or data, or from the inability to use the information or data.

.

High Performance Analyzer

GOOSE Simulator

SV Simulator

Device Under Test

Ethernet Switch

Client Simulator

tx

ty

t roundtrip

IED

Application Logic

to

copy value

Communi-cation processor

subscribed GOOSE messages

published GOOSE messages

Time Master