30900601-Consulting 09-version0.3

Test procedures for GOOSE performance according to IEC 61850-5 and IEC 61850-10 Version 0.3

On request of UCAIUG

March 9, 2010

Authors Richard Schimmel and Tao Xu

KEMA Consulting

| author : Richard Schimmel |  | reviewed : Bas Mulder |  |
| --- | --- | --- | --- |
| B 16 pages 2 annexes | RS | approved : Willem strabbing |  |

CONTENTS

page

1	Introduction	4

1.1	Test methodology	4

1.2	Test scope	6

1.3	Glossary	6

1.4	Identifications	7

2	Test environment	8

3	GOOSE performance testing	9

3.1	Message definitions	9

3.1.1	Published GOOSE used for ping-pong	9

3.1.2	Subscribed GOOSE used for ping-pong	9

3.1.3	Time correlated Subscribed GOOSE not used for ping-pong	10

3.1.4	Not subscribed GOOSE	10

3.1.5	Other communication tasks	10

3.2	Test cases	11

3.3	Test passed criteria	11

3.4	Test results	13

3.5	Detailed test procedure	14

# Introduction

The scope of the test is to benchmark the GOOSE performance against the performance classes as defined in IEC 61850-5. IEC 61850-5 clause 13 states:

13.7.1.1 Type 1A “Trip” : The trip is the most important fast message in the substation. Therefore, this message has more demanding requirements compared to all other fast messages. The same performance may be requested for interlocking, intertrips and logic discrimination between protection functions.

- For Performance Class P1, the total transmission time shall be in the order of half a cycle. Therefore, 10 ms is defined.

- For Performance Class P2/3, the total transmission time shall be below the order of a quarter of a cycle. Therefore, 3 ms is defined.

IEC 61850-5 defines the transmission time as follows

Figure 1: Transmission time definition IEC 61850-5

## Test methodology

To measure the transmission time as defined in IEC 61850-5 is not possible without special access to the internal data of the device. To enable "black-box" testing a test lab needs a different test methodology referred to as the "GOOSE ping-pong" method. This method is already in use for GOOSE conformance testing.

Figure 2:	Measure round trip time using GOOSE ping-pong method

The GOOSE ping-pong method focuses on the round trip time as defined in figure 2. The round trip time is the time interval between the arrival of a subscribed GOOSE message and the departure of the published GOOSE message:  troundtrip = (ty – tx).

The relation between the transfer time and roundtrip time is as follows:

# ttransfer 				= ta + tb + tc

# troundtrip 	= (ty – tx)	= tc* + tapplication + ta*

When PD1 and PD2 are the same we assume that the GOOSE publish and subscribe  communication processing times are the same in figure 1 and 2. In that case we can combine these equations into:

- ttransfer = troundtrip – tapplication + tb

We assume the network delay for a single Ethernet switch to be minimal (< 0.1ms).  Then we get

- ttransfer = troundtrip – tapplication

ta 			= GOOSE publish communication processing

tb 			= network delay of one GOOSE message

tc 			= GOOSE subscribe communication processing

tapplication 	= application time

The application time typically is the sum of the scan cycle wait time and the actual application logic processing time. On a scan cycle of for example 4 ms the average scan cycle wait time is about 2 ms (50% of scan cycle). The measured maximum – minimum roundtrip times will be close to the scan cycle. These metrics can be used to perform a plausibility check on the documented figures in the PIXIT document.

# According to IEC 61850-10 a test system shall measure latency time by generating a sequence of physical/virtual input triggers to the IED and measuring the time delay to the corresponding message generated by the IED. The mean latency time and the standard deviation shall be computed across the responses to 1000 input triggers.

## Test scope

The following items may have an impact on the GOOSE performance:

- Size of the published/subscribed GOOSE message (number of data set elements)

- Type of data set elements

- Which element of the data set is used

- Use of Functionally Constrained Data (FCD) or Functional Constrained Data Attributes (FCDA) in the dataset

- Number of subscribed GOOSE messages

- Time correlation of subscribed GOOSE messages state changes

- Number of non-subscribed GOOSE messages on the network

- Other communication tasks like MMS reporting, file transfer and/or Sampled Values when supported

This test procedure is intended as a benchmark for comparing relative performance of different IEDs. It defines standardized tests aimed at mimicking typical workload conditions. It does not test device performance under worst case load, worst case network conditions, or in a specific system application. Please refer to detailed vendor specifications for full description of the device capabilities, behaviour and limitations.

## Glossary

BRCB		Buffered Report Control Block

DUT		Device Under Test

GoCB		GOOSE Control Block

GOOSE	Generic Object Oriented System Event

ICD		IED configuration description in SCL-format

IED 		Intelligent Electronic Device

FCD		Functionally Constrainted Data

FCDA		Functionally Constrainted Data Attributes

PICS		Protocol Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

MAC		Media Access Control

ms			milliseconds

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

UCAIUG	UCA International Users Group

URCB		Unbuffered Report Control Block

VLAN		Virtual Local Area Network

## Identifications

The following table gives the exact identification of tested equipment and test environment used for this performance test.

| DUT | <identification and short name of the device under test> <hardware and software version> Performance class: P1 or P2/P3 |
| --- | --- |
| MANUFACTURER | <name, location of the manufacturer of the DUT> |
| PICS | <complete reference description of the PICS> |
| PIXIT | <complete reference description of the PIXIT> |
| ICD or SCD | <complete reference description of the SCL configuration file> |
| TEST INITIATOR | <name and address of test initiator> |
| TEST FACILITY | <name and address of test facility> |
| TEST ENGINEER | <name and e-mail address of test engineer> |
| TEST SESSION | <date and location of the test session> |
| ANALYSER | <name and type analyzer(s), version X.Y> |
| GOOSE SIMULATOR | <name and type GOOSE simulator> |
| SV SIMULATOR | <name and type SV simulator> |
| CLIENT SIMULATOR | <name and type client simulator> |
| TIME MASTER | <name and type of time master> |
| ETHERNET SWITCH | <name and type of Ethernet switch> |

The DUT shall be a regular production model. The only tuning that is allowed is ‘off-the-shelf’ configuration to minimize the application logic.

# Test environment

The test environment consists of the following components:

Figure 3: The test environment

The analyzer compares the published and the subscribed GOOSE messages from the DUT.

The client simulator and SV simulator are used to simulate specific communication during the test.

The DUT shall not be reconfigured during the performance test. The test procedures shall be designed in such a way that the DUT doesn't need to be reconfigured during the performance test.

# GOOSE performance testing

## Message definitions

The general message requirements are:

- Each GOOSE has unique multicast destination MAC address

- Each GOOSE has VLAN priority = 4 and VLAN ID = 0

- Each GOOSE has Test = FALSE, ConfRev = 1, NdsCom = FALSE

- The GOOSE datasets contain functionally constrained data attributes (FCDA)

- The BRCB or URCB datasets contain functionally constrained data (FCD)

### Published GOOSE used for ping-pong

The DUT will publish the following GOOSE:

Dataset					normal dataset = 4 Boolean data values and 4 qualities

large dataset = 20 Double Point data values, 20 Boolean Data values and 40 qualities

Transmission schema	Given by subscribed GOOSE, retransmission scheme as specified in the DUT documentation

GooseID					GPFPP_pong_normal, 		GPFPP_pong_large

GoCB name				GPFPPpongNormal, 			GPFPPpongLarge

Destination MAC			0x01 0C CD 01 00 01, 		0x01 0C CD 01 00 02

### Subscribed GOOSE used for ping-pong

The DUT will subscribe to the following GOOSE:

Dataset					normal dataset = 4 Boolean data values and 4 qualities

large dataset = 20 Double Point data values, 20 Boolean Data values and 40 qualities

Transmission schema	4 state changes of the 3rd data value element per second (about each 250 ms) uniform distributed over the scancycle

Retransmission at 4 and 32 ms (or more)

GooseID					GPFPP_ping_normal, GPFPP_ping_large

GocbRef	GPFPPpingNormalLD0/LLN0$GO$GPFPPpingNormal GPFPPpingLargeLD0/LLN0$GO$GPFPPpingLarge

Dataset name	GPFPPpingNormalLD0/LLN0$GPFPPpingNormal GPFPPpingLargeLD0/LLN0$GPFPPpingLarge

Destination MAC			0x01 0C CD 01 00 03																				0x01 0C CD 01 00 04

### Time correlated Subscribed GOOSE not used for ping-pong

The DUT will also subscribe to the following GOOSE:

Dataset	large dataset = 20 Double Point data values, 20 Boolean data values and 40 qualities

Transmission schema		5 subscribed GOOSE control blocks

Retransmission at 4, 32 and 256 ms (or more)

5 subscribed GOOSE each having one statechange of the 5th data value element at -4.0, -2.0, 0.0, 2.0 and 4.0 ms before and after the subscribed GOOSE state change used for ping-pong

GooseID					GPF_subscribed1..5

GocbRef	GPFsubscribed1..5LD0/LLN0$GO$GPFsubscribed1..5

Dataset name	GPFsubscribed1..5LD0/LLN0$GPFsubscribed1..5

Destination MAC	0x01 0C CD 01 00 05 to 0x01 0C CD 01 00 09

### Not subscribed GOOSE

Dataset	large dataset = 20 Double Point data values, 20 Boolean data values and 40 qualities

Transmission schema	100 GOOSE control blocks each with 1 state change per second (about every 10 ms) and 2 retransmissions per second (at 32 and 256 ms or more). The total number of these GOOSE messages will be at least 300 messages per second

GooseID					GPF_not_subscribed001..100

GocbRef                    GPFnotSubscribed001..100LD0/LLN0$GO$GPFnotSubscribed001..100

Dataset name				GPFnotSubscribed001..100LD0/LLN0$GPFnotSubscribed001..100

Destination MAC			0x01 0C CD 01 11 01 to 0x01 0C CD 01 11 64

### Other communication tasks

Report:	One client enables two BRCBs or when buffered reporting is not supported two URCBs with same data values (as FCD) as the normal and large dataset in the published GOOSE; 	The report will be send on data change with integrity 1 second and all supported optional fields

Sampled Values:	One merging unit is sending valid sampled value messages subscribed by the device with valid 4 currents and 4 voltages not activating any protection function

In case the DUT supports reporting one client shall be connected to the DUT during all test cases. In case the DUT supports Sampled Values valid sampled values shall be provided during all test cases.

## Test cases

The following table gives an overview of the test cases.

| Test ID | Subscribe (ping) | Publish (pong) | Time correlated Subscribed GOOSE not used for ping-pong | Not subscribed |
| --- | --- | --- | --- | --- |
| Gpf1 | Normal | Normal | No | No |
| Gpf2 | LARGE | LARGE | No | No |
| Gpf3 | Normal | Normal | YES | No |
| Gpf4 | Normal | Normal | No | YES |
| Gpf5 | LARGE | LARGE | YES | YES |

Note: "No" means that the GOOSE simulator will retransmit each GOOSE message without state change each second to prevent GOOSE subscribe errors.

## Test passed criteria

For performance class P1 the transmission limit is defined as 10 ms and 3 ms for P2/P3. According to IEC 61850-10 clause 7.2.1 the performance results are the average and standard deviation over 1000 input triggers and that the sum of the measured output and input latency shall be less than or equal to 80 % of the total transmission (because 20% is reserved for network latency).

In clause 1.1 we determined:  ttransfer = troundtrip – tapplication. The application time typically is the sum of the internal scan cycle wait time and the actual logic processing time. To represent  the worst case transfer time we set the actual logic processing time to zero (this means that the logic processing time is considered as part of the transfer time). As a result we get:

- Average application time 		=   50% of scan cycle

- Maximum application time 	= 100% of scan cycle

- Minimum application time 	=     0% of scan cycle

Now the transfer time can be calculated as follows:

- Average:	ttransfer.avg = troundtrip.avg – tapplication.avg 	= troundtrip.avg – scancycle/2

- Maximum:	ttransfer.max = troundtrip.max – tapplication.max 	= troundtrip.max – scancycle

- Minimum:	ttransfer.min = troundtrip.min – tapplication.min 	= troundtrip.min

Note: it is possible that the calculated maximum transfer time is less than the calculated minimum transfer time.

Plausibility checks:

- Documented scan cycle ≥ Measured scan cycle = troundtrip.max – troundtrip.min

- Documented scan cycle ≥ Measured standard deviation * 3.46   (for uniform distribution)

In case the measured scan cycle is more than the documented scan cycle, the documented scan cycle shall be adjusted. In case the DUT has an event driven method (no scan cycle) the scan cycle for the calculations is set to 0.0 ms.

To pass the performance test the criteria are:

- Gpf1 to Gpf4 test are passed when the calculated average, maximum and minimum transfer times are less than 80% of the applicable performance class limit (IEC 61850-10 clause 7.2.1 Note 1):

  - Performance class P1; 		ttransfer < 8.0 ms

  - Performance class P2/P3; 	ttransfer < 2.4 ms

- Gpf5 test is passed when the average, maximum and minimum calculated transfer times are less than 100% of the performance class limit:

  - Performance class P1; 		ttransfer <10.0 ms

  - Performance class P2/P3; 	ttransfer <  3.0 ms

The PIXIT document shall specify the GOOSE performance class and application logic scan cycle(s).

The DUT has passed the GOOSE performance test when all test cases are passed.

## Test results

Documented scan cycle 	= x.y ms

Measured scan cycle 		= x.y ms

Performance class 		= P1 or P2/P3

| Test ID | Minimum | Maximum | Average | Verdict |
| --- | --- | --- | --- | --- |
|  |  | Round-trip | Transfer | Round-trip | Transfer | Stddev |  |
| Gpf1 | x.y | x.y | x.y | x.y | x.y | x.yy | Passed |
| Gpf2 | x.y | x.y | x.y | x.y | x.y | x.yy | Failed |
| Gpf3 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf4 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf5 | x.y | x.y | x.y | x.y | x.y | x.yy |  |

## Detailed test procedure

| Gpf | GOOSE performance tests | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 5. The device publishes GOOSE pong messages with copied values 8. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start SV simulator when supported by DUT 4. Start high performance analyzer capture 5. Start GOOSE simulator as indicated below 6. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 7. Stop and save the analyzer capture 8. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf1 = with normal Subscribe (ping) Gpf2 = with large Subscribe (ping) Gpf3 = with normal Subscribe (ping) AND time correlated Subscribed GOOSE not used for ping-pong Gpf4 = with normal Subscribe (ping) AND not subscribed GOOSE Gpf5 = with large Subscribe (ping) AND not subscribed GOOSE AND time correlated Subscribed GOOSE not used for ping-pong |
| Comment The measured roundtrip times are: TEST AVERAGE MIN MAX STDEV Gpf1 .. .. .. .. Gpf2 .. .. .. .. Gpf3 .. .. .. .. Gpf4 .. .. .. .. Gpf5 .. .. .. .. |

ANNEX A: PIXIT template for GOOSE performance test

Introduction

This document specifies the protocol implementation extra information for testing (PIXIT) of the IEC 61850 GOOSE performance in the server device:  “<product>” with version “<version>”.

Together with the PICS this PIXIT forms the basis for a GOOSE performance test according to IEC 61850-5 and IEC 61850-10.

PIXIT for GOOSE performance test

| Description | Value / Clarification |
| --- | --- |
| Performance class | P1 or P2/P3 |
| GOOSE ping-pong processing method | Event driven based or Scan cycle based |
| Application logic scan cycle(s) |  |

ANNEX B: Template for GOOSE performance test certificate

IEC 61850 Certificate Level A/B1

| Issued to: | For the product: |
| --- | --- |
| <<MANUFACTURER>> << FULL ADDRESS>> | <<PRODUCT NAME>> <<VERSION NUMBER>> |

Issued by:  << TEST LAB >>

# The product has not shown to be non-conforming to:

IEC 61850-5 performance class <<P1 or P2/P3>>

The performance test has been performed according to the UCA International Users Group GOOSE performance Test Procedures version X.Y with product’s protocol implementation conformance statements: “<<PICS>>”, and product’s extra information for testing: “<<PIXIT>>”.

The following GOOSE performance has been measured:

| Scan cycle = x.y ms | Minimum | Maximum | Average |
| --- | --- | --- | --- |
| Roundtrip time | <<Minimum GpfX>> | <<Maximum GpfX>> | <<Average GpfX>> |
| Transfer time | <<Minimum GpfX>> | <<Maximum GpfX>> | <<Average GpfX>> |

This Certificate includes a summary of the test results as carried out at <<TESTLAB>> in <<COUNTRY>> with <<GOOSE simulator VERSION>> and <<Analyzer VERSION>>. This document has been issued for information purposes only, and the original paper copy of the test report: No. <<REPORT NUMBER>> will prevail.

<<LOCATION>>, <<DATE>>

<<Signature of responsible test engineer>>

<<Name of responsible test engineer>>

# 1 Level A - Independent Test lab with certified ISO 9000 or ISO 17025 Quality System

# Footnotes

http://en.wikipedia.org/wiki/Uniform_distribution_(continuous)

# Comments

We shall verify the correctness of this statement. As such we need to keep the non-subscribed GOOSE message testcase (removed at the previous telco)

# Text boxes

KEMA Nederland B.V.  Utrechtseweg 310, 6812 AR Arnhem  P.O. Box 9035, 6800 ET Arnhem  The Netherlands

T +31 26 3 56 91 11  F +31 26 3 89 24 77  contact@kema.com  www.kema.com  Registered Arnhem 09080262

Copyright © KEMA Nederland B.V., Arnhem, the Netherlands. All rights reserved.

This document  may be distributed to UCA international users group members only.

KEMA Nederland B.V. and/or its associated companies disclaim liability for any direct, indirect, consequential or incidental damages that may result from the use of the information or data, or from the inability to use the information or data.

.

High Performance Analyzer

GOOSE Simulator

SV Simulator

Device Under Test

Ethernet Switch

Client Simulator

tx

ty

troundtrip

Physical device PD1

Application Logic to

copy value

Communication processor

subscribed GOOSE messages

published GOOSE messages

Time Master

ta*

tapplication

tc*