Comments Form, maintained by Richard Schimmel (please send your comments to richard.schimmel@kema.com)

Updated 15 juni 2007 and 7 September 2007

| Document Date | Document |
| --- | --- |
| March 23 2007 | Conformance Test Procedures for Server Devices with IEC 61850-8-1 interface; Revison 2.0 |

| ID | Comment Author | Clause/ Subclause (Pg==Page) | Paragraph Figure/ Table TESTCASE | COMMENTS | Proposed change | OBSERVATIONS |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | KEMA | Technical | RpN4 | The SetURCBValues for ConfRev, SqNum should return: “object-access-denied”. The SetURCBValues for unknown DatSet should return: “object-value-invalid” or “invalid-address”? | See updated test procedure. |  |
| 2 | KEMA | Editorial | Ctl7 | AddCause and Error are not specied for the enhanced security control modes when the Check condition fails. | SBOes / DOes – command termination AddCause = Blocked-by-interlocking |  |
| 2 | KEMA | Editorial | Br general | BRCB configuration is possible when not pre-assigned to a specific client (using ClientLN in the SCL) | True, but will not add this pre-condition in each testcase. | No change |
| 2 | KEMA | Editorial | Br2 abstract | Replace URCB by BRCB |  |  |
| 2 | KEMA | Editorial | Br11, Rp9 | According to part 7-3 the timestamp should not be triggered at all. It will only be reported for GI and Integrity | Adjust expected result |  |
| 2 | KEMA | Editorial | Br13 | The expected is result is true only for those data objects in the LD (data objects from other LD may be reported) | Replace ”DUT does not send reports” by “DUT should not report data objects within the logical device” |  |
| 2 | KEMA | Editorial | CtlN2 | Tissue 334 is ed.2 and is not allowed; So the test procedure should describe the expected result without the tissue like it was before in version 1.1 | The second Select from same client should fail. The second SelectWithValue from same client should fail. |  |
| 2 | KEMA | Editorial | CtlN2 | What is step 8? | Replace step 8 by step 2 |  |
| 2 | KEMA | Editorial | CtlN3, CltN4, CtlN9, CtlN10, Ctln11, DOes2 | Part 7-2 fig 34 specifies NO command termination after SelectWithValue respond- (and Operate respond-). Part 8-1 table 69 maps the SelectWithValue respond- to 2 MMS pdu’s: a MMS Write response with failure and MMS informationReport with LastApplError. (in the test procedures this InformationReport with LastapplError is incorrectly referred to as CommandTermination) | Replace: DUT respond with SelectWithValue/Operate Response- and CommandTermination- with error “Operator Test Not OK” and Addcause “Position-reached” By: DUT respond with SelectWithValue/Operate Response- with LastApplError error “Operator Test Not OK” and Addcause “Position-reached” |  |
| 2 | KEMA | Editorial | CtlN3, CtlN10, CtlN11 | It is a local issue if the SBOes check is performed during the selectwithvalue phase or during Operate phase. So when the selectwithvalue respond is OK the operate should fail. | Add this possible expected result |  |
| 2 | KEMA | Editorial | DOes5, SBOes3, SBOes5 | For the step “keep old position” the AddCause may also be “time-limit-over”. Because the DUT may wait for a data change for the timeout period. | Add this AddCause to DOes5-step3, SBOes3-step4 and SBOes5-step6 |  |
| 2 | KEMA | Editorial | SBOes1 | Writing a non-existing (control) object will result in an MMS write error “object-non-existent” see SrvN3. Better test the incorrect access rights with the orCat. | Test the incorrect acces right by setting an incorrect orCat |  |
| 2 | KEMA | Editorial | SBOes2 | How should the server respond to the TimeActivatedRespond in step 3 | The DUT should send a TimeOper_rsp+ followed by timer_expired.timeOper_rsp+ followed by CmdTerm- |  |
| 2 | KEMA | Technical | New Rp, Br | Add new optional test case to verify that another client can not configure a pre-assigned BRCB/URCB |  |  |
| 2 | KEMA | Editorial | Rp11, Br13 | For Mod=Off, integrity and GI reports are still send with all the elements. For Mod/Beh datachanges are always reported! | Clarify to use trigger condition datachange and a non Mod/Beh dataobject inside the LD and force data changes using the equipment simulator |  |
| 2 | ABB | Technical | New Tm | A certified device transmitted the local timestamp in reports. This is not verfied in the current test procedures | Add a new (conditional) testcase “Tm3” that verifies the possibility to set Time-zone and daylight-saving on DUT and that the timestamps on the Reports are still transferred with UTC time. The time stamps of DR Files have to checked also |  |
|  | KEMA | Editorial | Rp7, Br7 | Adjust test procedure = verify both 2 data changes of one dataset element AND 1 data changes of 2 different dataset elements |  |  |
|  | KEMA | Editorial | Sg3 | Test procedures does not match with part 10. Sg3 should test the reading SG values not SGCB. | Replace GetSGCBValues by GetSGValues (FC=SG) |  |
| KEM | KEMA | Technical | New SgN | When a SG is being edited the SG values of theat group can not be read EditSG = 6 - The active SG may not the same as the EditSg | Add a new negative testcase to verify this behavior |  |
|  | KEMA | Editorial | SgN1b | ConfirmEditSGValues does not have a sgnumber as parameter SelectEditSG allows null value | Atteched |  |

Updated test procedures

| RpN4 | Incorrect configuration of URCB |  Passed  Failed  Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.1.1.2, Table 23 |
| Expected result 2. DUT sends SetURCBValues() response with data access error “temporarily-unavailable” 4. DUT sends SetURCBValues() response with data access error “object-access-denied” 5. DUT sends SetURCBValues() response with data access error “object-value-invalid” |
| Test description 1. Client configures and enables an available URCB 2. Client requests SetURCBValues() with one of the following "dyn" attributes RptID, DatSet, OptFlds, BufTm, TrgOps and/or IntgPd 3. Client disables the URCB 4. Client requests SetURCBValues() with one of the following "non-dyn" attributes ConfRev, SqNum and/or DatSet 5. Client requests SetURCBValues() with unknown DatSet (when DatSet is “dyn”) |
| Comment |

| SgN1b | Setting group definition services with wrong parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2., 13.3 IEC 61850-8-1 clause 16.2 PIXIT |
| Expected result DUT sends SelectEditSGValues Response- DUT sends SetSGValues Response- with applicable service error DUT sends ConfirmEditSGValues Response- DUT sends GetSGValues Response- |
| Test description Client requests SelectEditSGValues with out-of-range setting group Client requests SetSGValues with unknown object / wrong datatype Client requests ConfirmEditSGValues with unknown object Client requests GetSGValues with FC=SE unknown object |
| Comment |

| SgN3 | SetSGValues on selected setting group | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2.3 |
| Expected result 2. DUT sends SetSGValues Response- |
| Test description 1. Client requests SelectEditSG with setting group number null 2. Client requests a valid SetSGValues [FC=SE] |
| Comment |