30900601-Consulting 12-v0.1

Conformance Test Procedures for Client System with IEC 61850-8-1 Ed2 interface Revision 0.1b

On request of the UCA International Users Group

Arnhem,  April 22, 2012

Authors Marijn Flohil and Richard Schimmel

KEMA Consulting

Christof Pastors

Siemens AG

| author : Marijn Flohil | 01-10-2009 | reviewed : UCAIUG testsub |  |
| --- | --- | --- | --- |
| B 122 pages 3 annexes | MF | approved : UCAIUG testsub |  |

| Revision | Changes |
| --- | --- |
| Rev 0.1 April 2012 | Updated according to new Ed2 test cases up to page 25 |
| 0.1b | Reviewed pages 1-25 |

Remark: the detailed change history is not part of this report but is archived by KEMA.

CONTENTS

page

1	Introduction	5

1.1	Identifications	5

1.2	Background	6

1.3	Purpose of this document	6

1.4	Contents of this document	6

1.5	Glossary	7

2	References	7

2.1	Normative	7

2.2	Other	8

3	The Conformance test	8

3.1	Components in the test environment	8

3.2	Overview of the test suite	10

4	Test results	11

5	Conclusion and recommendations	12

5.1	Recommendations following from the test	12

Annex A 	Test procedures and results	13

A1 	Documentation and version control (IEC 61850-4)	13

A2	Configuration file (IEC 61850-6)	13

A3	Data model (IEC 61850-7-3 and IEC 61850-7-4)	14

A4	Mapping on MMS (IEC 61850-7-2 and IEC 61850-8-1)	15

A4.1	Block 1: Basic services	19

A4.2	Block 2: Data set	36

A4.2+	Block 2+: Data set definition	42

A4.3	Block 3: Substitution	45

A4.4	Block 4: Setting group selection	48

A4.4+	Block 4+: Setting group definition	50

A4.5	Block 5: Unbuffered Reporting	52

A4.6	Block 6: Buffered Reporting	66

A4.7	Block 7: Logging	82

A4.12	Block 12: Control	83

A4.12a	Block 12a: Direct Control	89

A4.12b	Block 12b: SBO Control	91

A4.12c	Block 12c: Direct Control with Enhanced Security	94

A4.12d	Block 12d: Enhanced SBO Control	96

A4.13	Block 13: Time and time synchronization	99

A4.14	Block 14: File transfer	102

A5	Mapping on GOOSE (IEC 61850-7-2 and IEC 61850-8-1)	107

A5.9b	Block 9b: GOOSE subscribe	108

A6	Free form testing	109

Annex B – Detailed description of test results	110

Annex C – PIXIT Template for Client	111

# Introduction

## Identifications

The following table gives the exact identification of the test environment used for this conformance test of a IEC 61850 CLIENT system.

| DUT | <complete description of the client Device Under Test, type, hardware / software version> |
| --- | --- |
| MANUFACTURER | <name, location of the manufacturer of the DUT> |
| PICS | <complete reference description of the PICS> |
| MICS | <complete reference description of the MICS> |
| TICS | <complete reference description of the TICS> |
| PIXIT | <complete reference description of the PIXIT> |
| SCD | <complete reference description of the SCD configuration file> |
| TEST INITIATOR | <the initiator of the test, name, address, contact person> |
| TEST FACILITY | <test facility name> <accredited/recognized to issue Level A/B/C Certificates> |
| TEST ENGINEER | <name and e-mail address of test engineer> |
| TEST SESSION | <date and location(s) of the test session> |
| SERVER SIMULATOR | <name and type conformance test simulator version X.Y with reference test suite, version X.Y and Test parameters file> |
| ANALYSER | <name and type analyzer, version X.Y> |
| HMI | <name and type equipment simulator> |
| TIME SERVER | <name and type of time master> |

<the TEST INITIATOR may provide the documents in digital or printed format>

## Background

<OPTIONAL, short description on the environment where the DUT will be used>

The TEST FACILITYs assignment was to answer the following question:

“Does the protocol implementation of the DUT, conform to the IEC 61850 standard and the PICS, MICS, TICS, PIXITdocuments as configured with SCD?”

To answer this question, TEST FACILITY has performed a conformance test of the IEC 61850 implementation in the DUT. This test has been performed according procedures and conditions set forth in IEC 61850 part 10 and UCA IUG Quality Assurance Program.

TEST FACILITY is accredited/recognized by the UCA IUG to perform formal IEC 61850 conformance tests and issue the Level A/B certificate.

## Purpose of this document

The purpose of this document is to describe the conformance test procedure and results of the TEST SESSION concerning the IEC 61850 implementation in the DUT.

The test procedures verify the client system under test against conformant servers.

The test results are the basis of the conformance statement.

## Contents of this document

Chapter 2 shows the list of relevant normative and other references, used to provide input for the conformance test.

Chapter 3 describes the various relevant components for the conformance test and their configuration as used in the conformance test, including the DUT. This chapter also gives an overview and introduction to the various test groups that together constitute the conformance test.

Chapter 4 and 5 give an overview and summary of the test results, the conclusion(s) and recommendations.

Appendix A specifies the detailed test procedures and their outcome, appendix B contains detailed comments on test results, for instance when a defect is detected, including the actual message flow if appropriate.

## Glossary

DUT		Device Under Test

HMI		Human machine interface

MICS		Model Implementation Conformance Statement

PICS		Protocol Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

SNTP		Simple Network Time Protocol

TICS		TISSUES Implementation Conformance Statement

TISSUE	Technical issue

TPCL		Test Procedure Change List

UCA IUG	UCA International Users Group

# References

## Normative

The tests defined in this document are based on the following IEC 61850 documents.

IEC 61850-4:2011, Communication networks and systems for power utility automation – Part 4: System and project management

IEC 61850-6:2009, Communication networks and systems for power utility automation – Part 6: Configuration description language for communication in electrical substations related to IEDs

IEC 61850-7-1:2011, Communication networks and systems for power utility automation – Part 7-1: Basic information and communication structure – Principles and models

IEC 61850-7-2:2010, Communication networks and systems for power utility automation – Part 7-2: Basic information and communication structure – Abstract communication service interface (ACSI)

IEC 61850-7-3:2010, Communication networks and systems for power utility automation – Part 7-3: Basic information and communication – Common data classes

IEC 61850-7-4:2011, Communication networks and systems for power utility automation – Part 7-4: Basic information and communication structure – Compatible logical node classes and data classes

IEC 61850-8-1:2011, Communication networks and systems for power utility automation – Part 8-1: Specific communication service mapping (SCSM) – Mappings to MMS (ISO/IEC 9506-1 and ISO/IEC 9506-2) and to ISO/IEC 8802-3

IEC 61850-10:2012, Communication networks and systems for power utility automation – Part 10: Conformance testing

## Other

ISO/IEC 9646-1:1994 OSI-Conformance testing methodology and framework, Part 1: General Concepts

UCA IUG: Quality Assurance Program for IEC Device Implementation Testing and Test System Accreditation and Recognition, Version 2.6, March 8, 2007

UCA IUG: Quality Assurance Program Addendum for IEC 61850 Specific Product Testing, Version 1.0, March 8, 2007

UCA IUG: Test Center Accreditation and Recognition Procedure

For IEC 61850 Device Testing, V1.1, August, 2006

TISSUES: http://www.tissues.iec61850.com

Test Procedures Change List (TPCL) for IEC 61850 client test procedures X.X,  Version YY, <date>

# The Conformance test

## Components in the test environment

The test environment consists of the following components:

- DUT

- SERVER SIMULATOR 1..N

- ANALYSER

- Ethernet HUB

- TIME SERVER

Figure 3.1 The test environment

The HMI can be integrated into the DUT (typically a substation control system) or in case the DUT is a protocol gateway the HMI is a protocol simulator with a HMI.

The server [simulator] requirements are:

- Modeling:

  - contain all common data classes supported by the DUT

  - contain several new data objects within a standard logical node

  - contain several new data attributes within a standard data object (common data class)

  - contain several new enum types and enum values

- Configuration:

  - one or more servers with preconfigured datasets with data objects

  - one or more servers with dynamic datasets (when supported by DUT)

  - one or more servers with report control block indexing

  - one or more servers without report control block indexing

- Communication:

  - support all conformance blocks supported by the DUT in one or more servers

  - support all ASCI services supported by the DUT

  - one or more servers with all supported control models

## Overview of the test suite

The abstract test cases and detailed test procedures are structured as follows:

- Documentation and version control (IEC 61850-4)

- Configuration file (IEC 61850-6)

- Data model (IEC 61850-7-3 and IEC 61850-7-4)

- Mapping of ACSI models and services (IEC 61850-7-2 and IEC 61850-8-1)

  - Application Association

  - Server & Logical Device & Logical Node & Data

  - Data Set

  - Substitution

  - Setting Group Control

  - Unbuffered and Buffered Reporting

  - Logging

  - Generic Substation Events

  - Control

  - Time Synchronization

  - File Transfer

  - Service Tracking

The PICS is used to select the applicable test procedures to be included in the test.

In general if a problem occurs on a connection to one server this shall have no impact on the connections to other servers.

# Test results

Table 4.1 in this Chapter describes the summary of the conformance test results. References shown in the table columns refer to references of individual test procedures in appendix A.

The Passed column indicates the test cases with test result Passed, the Failed column with test result Failed and the Inconclusive column for test result Inconclusive. For details refer to the applicable test procedure in Appendix A.

When all mandatory testcases within a conformance block are Passed or Inconclusive the DUT has passed the test for that conformance block.

Table 4.1	Summary of test results for DUT

| Test Group | Passed | Failed (*) | Inconclusive(*) |
| --- | --- | --- | --- |
| Documentation |  |  |  |
| Configuration |  |  |  |
| Data model |  |  |  |
| Conformance block |  |  |  |
| 1: Basic Exchange |  |  |  |
| 2: Data Set |  |  |  |
| 2+: Data Set Definition |  |  |  |
| 3: Substitution |  |  |  |
| 4: Setting Group Selection |  |  |  |
| 4+: Setting Group Definition |  |  |  |
| 5: Unbuffered Reporting |  |  |  |
| 6: Buffered Reporting |  |  |  |
| 7: Logging |  |  |  |
| 9: GOOSE Control Block |  |  |  |
| 12a: Direct control |  |  |  |
| 12b: SBO control |  |  |  |
| 12c: Enhanced Direct Control |  |  |  |
| 12d: Enhanced SBO control |  |  |  |
| 13: Time Sync |  |  |  |
| 14: File Transfer |  |  |  |
| 15a: Generic Tracking |  |  |  |
| 15b: Service Tracking |  |  |  |
| 15c: Control Tracking |  |  |  |
| TOTALS |  |  |  |

(*) column only when applicable

# Conclusion and recommendations

When all applicable testcases within a conformance block are Passed or Inconclusive the DUT has passed the test for that conformance block.

Based on the test results described in this report, TEST FACILITY declares the tested IEC 61850 implementation in the DUT has shown/not shown to be non-conforming to the IEC 61850 standard, PICS, MICS, TICS, PIXIT documents and SCD configuration.

## Recommendations following from the test

The following comments and recommendations apply for the DUT:

<Comments and Recommendations from TEST FACILITY>

# Annex A 		Test procedures and results

A1 	Documentation and version control (IEC 61850-4)

| Id | Test procedure | Verdict |
| --- | --- | --- |
| cDoc1 | Check if the major/minor software version in the PICS documentation and the DUT do match (IEC61850-4) |  |
| cDoc2 | Check if the major/minor software version in the PIXIT documentation and software version of the DUT does match (IEC61850-4). PIXIT shall indicate the required information as requested in the test cases in this document |  |
| cDoc3 | Check if the major/minor software version in the MICS documentation and software version of the DUT does match (IEC65180-4). MICS shall indicate which CDC’s and/or CDC parts are supported by the DUT, for example arrays |  |
| cDoc4 | Check if the major/minor software version in the TICS documentation and software version of the DUT does match (IEC61850-4). TICS shall indicate the supported technical issues. |  |

A2	Configuration file (IEC 61850-6)

| Id | Test procedure | Verdict |
| --- | --- | --- |
| cCnf1 | Check if the DUT process the data names, data types as configured in the SCL configuration file. |  |
| cCnf2 | Change at least 5 end-user configurable parameters that are displayed by the DUT in the SCL configuration file, configure the DUT using the SCL configuration file (using the supplied configuration tool) and check the updated configuration. Restore the original SCL file and re-configure the DUT to its original state. |  |
| cCnf3 | Verify that client can handle the ConfigRev management in SCL and exposed by the server in LLN0.NamPlt.configRev as described in the PIXIT. On a mismatch the DUT shall behave as described In the PIXIT (note that, if the PIXIT describes that the DUT does not check such a mismatch, no action is required by the DUT) |  |
|  | Verify all services declared in ICD services section matches PICS (conditional if ICD file exists) |  |

A3	Data model (IEC 61850-7-3 and IEC 61850-7-4)

| Id | Test procedure | Verdict |
| --- | --- | --- |
|  | Verify that the client can handle the maximum name length according to IEC 61850-7-2 Subclause 22.2 and SCSM??? and expands objects like SDOs correctly (PIXIT) |  |
|  | Verify that DUT supports the following naming conventions for the supported control blocks unbuffered report control block – not indexed unbuffered report control block – indexed buffered report control blocks setting group control block GOOSE control block Log control block |  |
|  | Verify that DUT can read and process the mandatory & optional attributes from the CDCs in part 7-3 unless stated otherwise in the MICS |  |

A4	Mapping on MMS (IEC 61850-7-2 and IEC 61850-8-1)

The test procedures are structured according to conformance blocks. The following table specifies which ACSI services, mapped on MMS, are mandatory/conditional for each conformance block for IEC 61850-8-1 Client systems.

Table A.4.1: ACSI services per conformance block for IEC 61850-8-1 Client systems

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | Associate Abort and/or Release | GetAllDataValues SetDataValues GetServerDirectory GetLogicalDeviceDirectory GetLogicalNodeDirectory (DATA) GetDataDirectory GetDataDefinition GetDataValues |
| 2: Data Set |  | GetDataSetValues SetDataSetValues GetLogicalNodeDirectory (DATA-SET) GetDataSetDirectory |
| 2+: Data Set Definition | CreateDataSet DeleteDataSet |  |
| 3: Substitution | SetDataValues | GetLogicalNodeDirectory (SGCB) |
| 4: Setting Group Selection | SelectActiveSG GetSGCBValues |  |
| 4+: Setting Group Definition | SelectEditSG, GetSGValues SetSGValues ConfirmEditSGValues |  |
| 5: Unbuffered Reporting | Receive Report GetURCBValues SetURCBValues | GetLogicalNodeDirectory (URCB) |
| 6: Buffered Reporting | Receive Report GetBRCBValues SetBRCBValues | GetLogicalNodeDirectory (BRCB) |
| 7: Logging | GetLCBValues GetLogicalNodeDirectory (LOG) QueryLogByTime or QueryLogAfter GetLogStatusValues | GetLogicalNodeDirectory (LCB) SetLCBValues |
| 9: GOOSE Control Block | GetGoCBValues GetLogicalNodeDirectory (GOCB) | SetGoCBValues |
| 12a: Direct control | Operate | TimeActivatedOperate |
| 12b: SBO control | Select, Operate | Cancel, TimeActivatedOperate |
| 12c: Enhanced Direct Control | Operate Receive CommandTermination | TimeActivatedOperate |
| 12d: Enhanced SBO control | SelectWithValue, Operate Receive CommandTermination | Cancel, TimeActivatedOperate |
| 13: Time sync | TimeSynchronization |  |
| 14: File transfer | GetServerDirectory(FILE) GetFileAttributeValues GetFile | SetFile DeleteFile |
| 15a: Generic Tracking | Receive Report |  |
| 15b: Service Tracking | Receive Report |  |
| 15c: Control Tracking | Receive Report |  |

The following table specifies which test procedures are mandatory/conditional for each conformance block. Conditions refer to the SCL - IED - Services section, the PICS or PIXIT.

Table A.4.2: Test procedures per conformance block

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | cAss1, cAss2, cAss3, cAss4, cAssN1, cAssN4, cAssN5, cAssN6 | Automatic startup: cAssN7 GetXxxDirectory: cSrv1, cSrv2, cSrv3, cSrv4, cSrvN1 GetDataValues: cSrv5, cSrv7 cSrvN3 SetDataValues: cSrv6, cSrv9, cSrvN4 GetAllDataValues: cSrv8, cSrvN2 Quality: cSrvN5 TimeQuality: cSrvN6 |
| 2: Data Sets |  | GetDataSetValues: cDs3, cDsN2 SetDataSetValues: cDs4, cDsN3 GetLogicalNodeDirectory(DATA-SET): cDs1, cDsN1a GetDataSetDirectory: cDs2, cDs5, cDsN1b |
| 2+: Data Set Definition | cDs6, cDsN4 | DeleteDataSet: cDs7, cDsN5 |
| 3: Substitution | cSub1 | cSub2, cSub3 |
| 4: Setting Group Selection | cSg2, cSgN1 | GetLogicalNodeDirectory(SGCB): cSg1 GetSettingGroupValues: Sg3 |
| 4+: Setting Group Definition | cSg3, cSg4 |  |
| 5: Unbuffered Reporting | cRp3, cRp4, cRp5, cRp8, cRp9, cRp10, cRpN2, cRpN3, cRpN7, cRpN8 | GetLogicalNodeDirectory(URCB): cRp1, cRpN1 SetURCBValue(RptID or Datset): cRp2 Buffer time: cRp6 General interrogation: cRp7 Reserved: cRpN4 Unsupported optflds: cRpN5 Unsupported trigger: cRpN6 |
| 6: Buffered Reporting | cBr3, cBr4, cBr5, cBr8, cBr9, cBr10, cBr11, cBr12, cBrN2, cBrN3, cBrN7, cBrN8, cBrN9 | GetLogicalNodeDirectory(BRCB): cBr1, cBrN1 SetBRCBValue(RptID or Datset): cBr2 Buffer time: cBr6 General interrogation: cBr7 Purge buffer: cBr13 Reserved: cBrN4 Unsupported optflds: cBrN5 Unsupported trigger: cBrN6 |
| 12a: Direct control | cCtl4, cCtlN1, cDOns1, cDOns2 | Test: cCtl1 Check: cCtl2 Change control model: cCtl3 |
| 12b: SBO control | cCtl4, cCtlN1, cSBOns1, cSBOns2, cSBOns3 | Test: cCtl1 Check: cCtl2 Change control model: cCtl3 Cancel: cSBOns4 |
| 12c: Enhanced Direct Control | cCtl4, cCtlN1, cDOes1, cDOes2 | Test: cCtl1 Check: cCtl2 Change control model: cCtl3 |
| 12d: Enhanced SBO control | cCtl4, cCtlN1, cSBOes1, cSBOes2, cSBOes3 | Test: cCtl1 Check: cCtl2 Change control model: cCtl3 Cancel: cSBOes4 |
| 13: Time sync | cTm1 | Optional: cTm2 TimeQuality: cTmN2 ClockNotsynchronized: cTmN1 |
| 14: File transfer | cFt1, cFt2, cFt3, cFtN1, cFtN2 | SetFile: cFt4, cFtN3 DeleteFile: cFt5 |
| 15a: Generic Tracking |  | Common: cTrk17 |
| 15b: Services Tracking |  | Reporting: cTrk1, cTrk2 Logging: cTrk3 GOOSE control block: cTrk4 SMV: cTrk5, cTrk6 Setting Group: cTrk7 |
| 15c: Control Tracking |  | Control: cTrk8, cTrk9, ctrk10, cTrk11, cTrk12, cTrk13, cTrk14, cTrk15, cTrk16 |

Note1: cAssN2 and cAssN3 are not applicable for part 8-1

Note2: Time activated control and logging test procedures are not available yet ???

Note3: cCtlN2 is out of scope for IEC 61850 conformance testing

The focus of the conformance test is the application layer. For IEC 61850-8-1 the communication services are mapped on the reliable TCP transport layer. As such the testing of transport related errors like “no response” and “delayed response” are out-of-scope. These are implicitly tested by disconnecting the Ethernet cable between the server and the switch.

In general if a problem occurs on a connection to one server this may have no impact on the connections to other servers.

The following paragraphs describe the abstract test cases and the corresponding detailed test procedure.

## A4.1	Block 1: Basic services

Abstract test cases for Application Association

| Test case | Test case description |
| --- | --- |
|  | Associate and force client to release a TPAA (IEC 61850-7-2 8.3, 8-1 10.2) |
|  | Force the client to associate with maximum number of servers simultaneously (PIXIT). |
|  | Verify that losing and restoring the TPAA between DUT and server has no effect on existing TPAA between DUT and other servers. |
|  | Verify the client can handle servers with small (4k) and large (64k) MMS PDU size, the client should keep on proposing it’s original MMS PDU size |

Note1: The client is always considered to be the calling node

| Test case | Test case description |
| --- | --- |
|  | Associate and server responds with negative response due to AccessPoint mismatch. |
|  | Associate and server responds with negative response due to AuthenticationParameter mismatch. |
|  | Associate and server releases TPAA (IEC 61850-7-2 8.3). DUT should try to re-establish the association after the configured period (PIXIT). |
|  | Associate and server-abort TPAA (IEC 61850-7-2 8.3). DUT should try to re-establish the association after the configured period (PIXIT). |
|  | Associate and server denies TPAA (IEC 61850-7-2 8.3). DUT should try to re-establish the association after the configured period (PIXIT). |
|  | Disconnect the communication interface, the DUT should detect link lost within a specified period. |
|  | Interrupt and restore the power supply, the DUT shall automatically establish the configured associations when ready (PIXIT). |

Detailed test procedures for Application Association

| cAss1 | Associate and force client to release a TPAA (IEC 61850-7-2, 8.3) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 1. DUT accepts Associate.response+ from server 2. DUT returns to “state” where it is able to start a new TPAA with the same server |
| Test description Set-up a TPAA with one server Force DUT to release or abort TPAA Repeat step 1 and 2, 10 times |
| Comment May also optionally use abort in place of release according to PIXIT |

| cAss2 | Associate to maximum servers | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 1. DUT accepts Associate.response+ from all servers 2. DUT returns to “state” where it is able to start new TPAAs with the same servers |
| Test description Set-up a TPAA with the maximum number of servers as specified in the PIXIT Force DUT to release or abort all open TPAAs Repeat step 1 and 2, 10 times |
| Comment Tested with X servers |

| cAss3 | Restore lost association | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3, figure 7 and 8 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 1. DUT accepts Associate.response+ from all servers 2. DUT detects connection loss and tries to reconnect to the server. All other TPAAs shall remain active. 3. DUT successfully restores the connection to the server 4. DUT receives and accepts the Release.response+ from all servers or receives and accepts the abort response+ from all servers |
| Test description Set-up a TPAA with at least two servers Force a TPAA disconnect for one server Restore the situation where the disconnected server is able to accept a new TPAA Force DUT to release or abort all TPAAs |
| Comment Client can detect via KEEPALIVE or MMS mechanism Need additional switch between client and existing hub/switch |

| cAss4 | Verify that the client can handle servers with small and large MMS PDU size | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 1. Client accepts Associate.response+ from all servers 2. DUT receives and accepts the Release.response+ from all servers or receives and accepts the abort response+ from all servers |
| Test description Set-up a TPAA with at least two servers where one server has a small PDU size (4k), and the other server has a large PDU size (64k). Force DUT to release or abort all open TPAAs |
| Comment Tested with X servers |

| cAssN1 | Access point mismatch | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-8-1 clause 10.2, 25.3.1 and table 132 PIXIT |
| Expected result 2. The TPAA fails 4. The TPAA fails 6. The TPAA fails |
| Test description 1. Set-up the DUT and one server to have a mismatching Transport Selector 2. Set-up a TPAA between the DUT and the server 3. Set-up the DUT and one server to have a mismatching Presentation Selector 4. Set-up a TPAA between the DUT and the server 5. Set-up the DUT and one server to have a mismatching Session Selector 6. Set-up a TPAA between the DUT and the server |
| Comment |

| cAssN2 | AuthenticationParameter mismatch. | Out of scope |
| --- | --- | --- |
| PIXIT |
| Expected result |
| Test description |
| Comment This testcase is not applicable for edition 2 of IEC 61850. |

| cAssN3 | Server release | Out of scope |
| --- | --- | --- |
| Expected result |
| Test description |
| Comment This testcase is out of scope for the IEC 61850 Client conformance test. |

| cAssN4 | Server abort | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result DUT accepts Associate.response+ from server DUT receives and responds correctly to the abort request from the server |
| Test description 1. Set-up a TPAA with one server 2. Force server to abort TPAA 3. Repeat step 1 and 2, 10 times |
| Comment |

| cAssN5 | Server deny | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result DUT detects the Association failure and responds as specified in the PIXIT. |
| Test description 1. Set-up test configuration with at least two servers 2. Force the DUT to perform an Associate request for all servers which is denied (response-) by one server caused by a mismatching session or presentation selector 3. Repeat step 1 and 2, 10 times |
| Comment |

| cAssN6 | Detection of lost link | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 3. DUT shall detect the lost link and shall try to reconnect to the server 4. DUT shall set-up a TPAA with the server |
| Test description 1. Connect the DUT and one server to a hub 2. Set-up a TPAA with the server 3. Disconnect the physical link, between the hub and the server, some seconds longer than the timeout specified in the PIXIT 4. Reconnect the Ethernet cable |
| Comment |

| cAssN7 | Power supply interrupt | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.3 IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 3. DUT behaves as specified in the PIXIT. |
| Test description 1. Set-up a TPAA between DUT and all servers as configured in SCL 2. Interrupt the power supply to DUT 3. Restore the power supply to DUT |
| Comment |

Abstract test cases for server, logical device, logical node and data

| Test case | Test case description |
| --- | --- |
|  | If the DUT implements Autodescription, (See Note 1) force the DUT to start the autodescription and check the DUT requests a GetServerDirectory(LOGICAL-DEVICE) to all the logical devices of the configured servers (see Note 2) (IEC 61850-7-2 Subclause 7.2.2) |
|  | If the DUT implements Autodescription, for each GetServerDirectory(LOGICAL-DEVICE) response check the DUT issues a GetLogicalDeviceDirectory request (IEC 61850-7-2 Subclause 9.2.1) |
|  | If the DUT “implements Autodescription”, for each GetLogicalDeviceDirectory response check the DUT issues a GetLogicalNodeDirectory(DATA) request (IEC 61850-7-2 Subclause 10.2.2) |
|  | If the DUT “implements Autodescription”, for a subset of the GetLogicalNodeDirectory(DATA) response check the DUT issues at least one of the following services: GetDataDirectory request and check response (IEC 61850-7-2 Subclause 11.4.4) GetDataDefinition request and check response (IEC 61850-7-2 Subclause 11.4.5) |
|  | Verify that after start-up the DUT is able to update the process values of the configured servers. |
|  | Request a SetDataValues of the different basic types (with for example FC=CF) and check the services (IEC 61850-7-2 Subclause 11.4.3) |
|  | Request GetDataValues and check if the DUT updates its model (IEC 61850-7-2 Subclause 11.4.2) |
|  | Request GetAllDataValues for the required functional constraints and check if the DUT updates its model (IEC 61850-7-2, 9.2.3) |
|  | Verify that the client is able to set/reset blkEna (IEC 61850-7-3 Subclause 6.2.6) |

NOTE 1  Implement Autodescription means that there is a way to configure the DUT to update the image of the model of one of the servers it has to communicate with using the ACSI services.

NOTE 2  Configured servers means the servers the client DUT is configured to communicated with. The client DUT at least needs to know the parameters to establish an association with them.

| Test case | Test case description |
| --- | --- |
|  | If the DUT implements autodescription, force the DUT to start the autodescription and check the DUT still communicates with other servers when it requests the following services with negative response: GetServerDirectory(LOGICAL-DEVICE), GetLogicalDeviceDirectory, GetLogicalNodeDirectory(DATA), GetDataDirectory, GetDataDefinition. |
|  | Check that the DUT is able to communicate with other connected servers after a request for GetAllDataValues fails in the following circumstances: The response is negative. The response comes with mismatching data objects. |
|  | Check that the SUT is able to communicate with other connected servers after a request for GetDataValues fails in the following circumstances: The response is negative. The response comes with mismatching data objects. The value is out of the valid range for this data. |
|  | Check that the DUT is able to communicate with other connected servers after a request for SetDataValues fails in the following circumstances: The response is negative. One of the data values is read-only |
|  | If DUT detects/notify changes in the “Quality” attribute, force the SERVER SIMULATOR to change the values in the Quality of the measured/status values monitored by the DUT and check the behaviour described in the PIXIT. |
|  | If SUT detects/notify changes in the timeStamp’s “TimeQuality” attribute, force a server to change the values in the TimeQuality of the measured/status values monitored by the SUT and check the behaviour described in the PIXIT. |

Detailed test procedures for server, logical device, logical node and data

| cSrv1 | GetServerDirectory(LOGICAL-DEVICE) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8, 9, 10 IEC 61850-8-1 clause 11, 12, 13 |
| Expected result 2. SUT accepts a GetServerDirectory.Response+ from the server |
| Test description 1. Set-up a TPAA with at least two servers 2. SUT request for each server a GetServerDirectory(LOGICAL-DEVICE) 3. Continue with cSrv2 |
| Comment |

| cSrv2 | GetLogicalDeviceDirectory | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8, 9, 10 IEC 61850-8-1 clause 11, 12, 13 |
| Expected result 1. SUT accepts a GetLogicalDeviceDirectory.Response+ from the server |
| Test description SUT request for each responded LogicalDevice a GetLogicalDeviceDirectory Continue with cSrv3 |
| Comment |

| cSrv3 | GetLogicalNodeDirectory | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8, 9, 10 IEC 61850-8-1 clause 11, 12, 13 |
| Expected result 1. SUT accepts a GetLogicalNodeDirectory(DATA).Response+ from the server |
| Test description SUT request for each responded LogicalNode a GetLogicalNodeDirectory(DATA) Continue with cSrv4 |
| Comment |

| cSrv4 | GetDataDirectory / GetDataDefinition | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8, 9, 10 IEC 61850-8-1 clause 11, 12, 13 |
| Expected result 1. SUT accepts a GetDataDirectory/GetDataDefinition.Response+ from the server |
| Test description SUT request for responded dataobjects a GetDataDirectory/GetDataDefinition Release the TPAA with all servers |
| Comment GetDataDirectory and GetDataDefinition are mapped to the MMS GetVariableAccessAttributes service |

| cSrv5 | GetDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.3, 10.4.2 IEC 61850-8-1 clause 12.3.2, 13.2.1 PIXIT |
| Expected result 2-3. SUT accepts a GetDataValues.Response+ from server |
| Test description Set-up a TPAA with one server SUT request GetDataValues of at least two data attributes SUT request GetDataValues of at least two data objects |
| Comment |

| cSrv6 | SetDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.2 PIXIT |
| Expected result 2. SUT accepts a SetDataValues.Response+ from server |
| Test description Set-up a TPAA with one server SUT request SetDataValues on a writable data attribute with FC = CF, DC, SP or on a non-standard EX with one of the basic type: boolean, integer, float, bitstring or enumerated. |
| Comment |

| cSrv7 | GetAllDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.3, 10.4.2 IEC 61850-8-1 clause 12.3.2, 13.2.1 PIXIT |
| Expected result 2. SUT accepts a GetAllDataValues.Response+ from server |
| Test description Set-up a TPAA with one server SUT request GetAllDataValues of at least two Functional Constraints |
| Comment |

| cSrvN1 | GetLogicalDeviceDirectory & GetDataDefinition negative | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.2.1, 10.4 IEC 61850-8-1 clause 11, 12, 13 PIXIT |
| Expected result 1,3,5,7,9,11. SUT associates with the server and responds as specified in PIXIT. SUT shall continue with the other servers 2,4. SUT accepts a GetLogicalDeviceDirectory.Response- from the server and continues as specified in PIXIT 6,8. SUT accepts a GetDataDefinition.Response- from the server and continues as specified in PIXIT 10,12. SUT receives a GetDataDefinition response and continues as specified in PIXIT |
| Test description 1. Reconfigure/rename the LogicalDevice for one server only and restart the server 2. SUT requests GetLogicalDeviceDirectory of the previously known logical device 3. Reconfigure/rename the LogicalNode (in a valid existing logical device) for one server only and restart the server 4. SUT requests GetLogicalDeviceDirectory of the previously known logical node 5. Reconfigure/rename a data object (in a valid existing logical node) for one server only and restart the server 6. SUT requests GetDataDefinition of the previously known data object 7. Reconfigure/rename a data attribute (in a valid existing data object) for one server only and restart the server 8. SUT requests GetDataDefinition of the previously known data attribute 9. Reconfigure CDC type of a data object (more data attributes then expected) for one server only and restart the server 10.SUT requests GetDataDefinition of a known data object with more data attributes then expected 11.Reconfigure CDC type of a data object (less attributes then expected) for one server only and restart the server 12.SUT requests GetDataDefinition of a known data object with less attributes then expected |
| Comment See IEC 61850-7-4 for valid LogicalNode Names. For IEC 61850-8-1: GetLogicalNodeDirectory(DATA) and GetLogicalDeviceDirectory are mapped to the MMS GetNamedList service GetDataDirectory and GetDataDefinition are mapped to the MMS GetVariableAccessAttributes service |

| cSrvN2 | GetAllDataValues negative | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.3 IEC 61850-8-1 clause 12.3.2 PIXIT |
| Expected result 1,3,5,7. SUT associates with the server and responds as specified in PIXIT. SUT shall continue with the other servers 2,4. SUT accepts a GetAllDataValues.Response- from the server and continues as specified in PIXIT 6,8. SUT receives a GetAllDataValues response and continues as specified in PIXIT |
| Test description 1. Reconfigure/rename the LogicalDevice for one server only and restart the server 2. SUT requests GetAllDataValues of the previously known logical device 3. Reconfigure/rename the LogicalNode (in a valid existing logical device) for one server only and restart the server 4. SUT requests GetAllDataValues of the previously known logical node 5. Reconfigure CDC type of a data object (more data attributes then expected) for one server only and restart the server 6. SUT requests GetAllDataValues of a known data object with more data attributes then expected 7. Reconfigure CDC type of a data object (less attributes then expected) for one server only and restart the server 8. SUT requests GetAllDataValues of a known data object with less attributes then expected |
| Comment See IEC 61850-7-4 for valid LogicalNode Names. |

| cSrvN3 | GetDataValues negative | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.2 IEC 61850-8-1 clause 13.2.1 PIXIT |
| Expected result 1,3,5,7,9,11.SUT associates with the server and responds as specified in PIXIT. SUT shall continue with the other servers 2,4,6,8. SUT accepts a GetDataValues.Response- from the server and continues as specified in PIXIT 10,12. SUT receives a GetDataValues response and continues as specified in PIXIT |
| Test description 1. Reconfigure/rename the LogicalDevice for one server only and restart the server 2. SUT requests GetDataValues of the previously known logical device 3. Reconfigure/rename the LogicalNode (in a valid existing logical device) for one server only and restart the server 4. SUT requests GetDataValues of the previously known logical node 5. Reconfigure/rename a data object (in a valid existing logical node) for one server only and restart the server 6. SUT requests GetDataValues of the previously known data object 7. Reconfigure/rename a data attribute (in a valid existing data object) for one server only and restart the server 8. SUT requests GetDataValues of the previously known data attribute 9. Reconfigure CDC type of a data object (more data attributes then expected) for one server only and restart the server 10.SUT requests GetDataValues of a known data object with more data attributes then expected 11.Reconfigure CDC type of a data object (less attributes then expected) for one server only and restart the server 12.SUT requests GetDataValues of a known data object with less attributes then expected |
| Comment |

| cSrvN4 | SetDataValues negative | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.2 PIXIT |
| Expected result 1,3,5,7,9,11.SUT associates with the server and responds as specified in PIXIT. SUT shall continue with the other servers 2,4,6,8,13. SUT accepts a SetDataValues.Response- from the server and continues as specified in PIXIT 10,12. SUT receives a SetDataValues response and continues as specified in PIXIT |
| Test description 1. Reconfigure/rename the LogicalDevice for one server only and restart the server 2. SUT requests SetDataValues of the previously known logical device 3. Reconfigure/rename the LogicalNode (in a valid existing logical device) for one server only and restart the server 4. SUT requests SetDataValues of the previously known logical node 5. Reconfigure/rename a data object (in a valid existing logical node) for one server only and restart the server 6. SUT requests SetDataValues of the previously known data object 7. Reconfigure/rename a data attribute (in a valid existing data object) for one server only and restart the server 8. SUT requests SetDataValues of the previously known data attribute 9. Reconfigure CDC type of a data object (more data attributes then expected) for one server only and restart the server 10.SUT requests SetDataValues of a known data object with more data attributes then expected 11.Reconfigure CDC type of a data object (less attributes then expected) for one server only and restart the server 12.SUT requests SetDataValues of a known data object with less attributes then expected 13.SUT requests SetDataValues of an existing read-only data attribute |
| Comment |

| cSrvN5 | Quality values | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.2 IEC 61850-8-1 clause 13.2.1 PIXIT |
| Expected result 1. SUT processes the quality as specified in the PIXIT. |
| Test description 1. Change the value of attribute q of a data object of one server to: Validity: Invalid Validity: Questionable – Failure = true Validity: Questionable – OldData = true Source = Substituted (by another client) Test = true OperatorBlocked = true |
| Comment |

| cSrvN6 | Time Quality values | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.2 IEC 61850-8-1 clause 13.2.1 PIXIT |
| Expected result 1-3. SUT processes the time quality as specified in the PIXIT. |
| Test description 1. Force server to respond with data object with time quality “clock failure” 2. Force server to respond with data object with time quality “clock not synchronised” 3. Force server to respond with data object with time quality “leap seconds known” |
| Comment |

## A4.2	Block 2: Data set

| Test case | Test case description |
| --- | --- |
|  | Force SUT to request a GetLogicalNodeDirectory(DATASET) of the Logical Nodes of the configured servers. |
|  | Check that the SUT can perform a GetDataSetDirectory request for all the DataSets of the server. |
|  | Check that the SUT can send a GetDataSetValues request and handle the response |
|  | Check SUT can request a SetDataSetValues and handle the respond |
|  | Verify that the client checks the pre-configured datasets in the SCD file. If any deviation is detected the SUT behaves as specified in the PIXIT |

| Test case | Test case description |
| --- | --- |
|  | Check that the SUT still communicates with other servers when the following requests return a negative response: GetLogicalNodeDirectory (DATASET) GetDataSetDirectory |
|  | Check that the SUT still communicates with other servers properly when it performs a GetDataSetValues request on one server and one of the following situations happens: The response is negative. The response contains more/less members than expected The response contains reordered members of different types The response contains reordered members of the same type |
|  | Check that the SUT still communicates with other servers properly when it performs a SetDataSetValues request on one server and the response is negative. |

Detailed test procedures for Data Set

| cDs1 | GetLogicalNodeDirectory(DATASET) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 IEC 61850-8-1 clause 12.3.1 |
| Expected result 1. SUT accepts the respond. |
| Test description 1. Force SUT to perform a GetLogicalNodeDirectory(DATASET) request for each server and logical device |
| Comment For IEC 61850-8-1 the GetLogicalNodeDirectory(DATASET) is mapped on a GetNameList and a logical device as parameter |

| cDs2 | GetDataSetDirectory | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.6 IEC 61850-8-1 clause 14.3.5 |
| Expected result 1. SUT accepts the respond. |
| Test description 1. Force SUT to perform a GetDataSetDirectory request for the data sets used by the SUT |
| Comment |

| cDs3 | GetDataSetValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.2 IEC 61850-8-1 clause 14.3.1 PIXIT |
| Expected result 1. SUT accepts the respond. |
| Test description 1. Force SUT to perform a GetDataSetValues request |
| Comment |

| cDs4 | SetDataSetValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.3 IEC 61850-8-1 clause 14.3.2 PIXIT |
| Expected result 1. SUT accepts the respond. |
| Test description 1. Force SUT to perform a SetDataSetValues request |
| Comment |

| cDs5 | Pre-configured dataset deviations | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3 IEC 61850-8-1 clause 14.3 PIXIT |
| Expected result 3. SUT responds as specified in PIXIT on the reconfigured datasets. |
| Test description 1. Stop one server 2. Reconfigure the server to force the following mismatches in different datasets: Insert a new dataset element in the middle of a dataset Delete a dataset element in the middle of a dataset Reorder 2 dataset members in a dataset of a different data type Reorder 2 dataset members in a dataset of the same data type 3. Start the server and force the SUT to perform a GetDataSetDirectory request on all the datasets used by the SUT |
| Comment |

| cDsN1 | GetLogicalNodeDirectory(DATASET).response- and GetDataSetDirectory.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.3.6 IEC 61850-8-1 clause 12.3.1, 14.3.5 PIXIT |
| Expected result 4. The SUT processes the negative response and continues as specified in PIXIT 5. The SUT processes the response as specified in the PIXIT 6. The SUT does not send the request or behaves as specified in PIXIT |
| Test description a) 1. Stop one server 2. Reconfigure the server in the following way: Rename a dataset in one logical device Add a dataset in another logical device Rename another logical device 3. Start the server 4. Force the SUT to perform a GetLogicalNodeDirectory(DATA-SET) request for the previously known logical device 5. Force the SUT to perform a GetLogicalNodeDirectory(DATA-SET) request for the logical device which contains the dataset that was newly added b) 6. Force the SUT to perform a GetDataSetDirectory request for the previously known dataset |
| Comment |

| cDsN2 | GetDataSetValues response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.2 IEC 61850-8-1 clause 14.3.1 PIXIT |
| Expected result 3. The SUT responds as specified in PIXIT. |
| Test description 1. Stop one server 2. Configure the server SCL file in the following way (one change per dataset): Delete a dataset The number of members is more/less then expected: add a dataset element in the middle of a dataset remove a dataset element from the middle of the dataset change the order of dataset members, hereby changing the order of the datatypes change the order of dataset members, without changing the order of the datatypes Start the server and force the SUT to perform a GetDataSetValues request on the removed/altered dataset |
| Comment |

| cDsN3 | SetDataSetValues response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.3 IEC 61850-8-1 clause 14.3.2 PIXIT |
| Expected result 1. The SUT processes the response as specified in the PIXT |
| Test description 1. Force the SUT to perform a SetDataSetValues request on a dataset that does not exist in the server |
| Comment |

## A4.2+	Block 2+: Data set definition

| Test case | Test case description |
| --- | --- |
|  | Check if the SUT can send a correct CreateDataSet request for: a non-persistent dataset a persistent dataset |
|  | Request a DeleteDataSet service and check the client sends the request properly and is able to process the response of the server. |

| Test case | Test case description |
| --- | --- |
|  | Check if the SUT still communicates with other servers after it receives a CreateDataSet.response- |
|  | Check if the SUT still communicates with other servers after it receives a DeleteDataSet.response- |

Detailed test procedures for Data Set definition

| cDs6 | CreateDataSet | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT |
| Expected result 1a) The SUT sends a correct CreateDataSet request 1b) The SUT sends a correct CreateDataSet request |
| Test description 1. Force SUT to: Perform a CreateDataSet request to create a non-persistent dataset Perform a CreateDataSet request to create a persistent dataset |
| Comment |

| cDs7 | DeleteDataSet | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.5 IEC 61850-8-1 clause 14.3.4 PIXIT |
| Expected result 1a). SUT sends correct DeleteDataset request 1b). SUT sends correct DeleteDataset request |
| Test description 1. Force SUT to: Perform a DeleteDataSet request on a non-persistent dataset Perform a DeleteDataSet request on a persistent dataset |
| Comment |

| cDsN4 | CreateDataSet.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT |
| Expected result 1. SUT behaves as specified in the PIXIT |
| Test description 1. Force SUT the send a CreateDataSet request that returns a CreateDataSet.response- |
| Comment |

| cDsN5 | DeleteDataSet.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.5 IEC 61850-8-1 clause 14.3.4 PIXIT |
| Expected result 1. SUT behaves as specified in the PIXIT |
| Test description 1. Force SUT to send a DeleteDataSet request that returns a DeleteDataSet.response- |
| Comment |

## A4.3	Block 3: Substitution

|  | Verify SUT can enable substitution, enter a substituted value and disable substitution |
| --- | --- |
|  | Verify SUT can proces the source “substituted” for substituted values |
|  | Verify SUT can proces the source “substituted” for values substituted by another client |

Detailed test procedures for Substitution

| cSub1 | Substitute a value | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 |
| Expected result 1. SUT sends successful SetDataValues requests for the values with functional constraint SV 2. SUT successfully enables substitution 3. SUT successfully disables substitution |
| Test description 1. SUT substitutes the values of data objects in one server by another valid value of the following type: single point status double point status enumerated status integer measurand floating point measurand quality 2. SUT enables substitution 3. SUT disables substitution |
| Comment |

| cSub2 | Verify that SUT can process the source "substituted" for substituted value | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 |
| Expected result 2. SUT succesfully enables substitution 3. SUT processes the new substituted value and quality with source “substituted” when transmitted by the report or GetDataValues response 4. SUT succesfully disables substitution 5. SUT processes the original process value and quality with source “process” when transmitted by the GetDataValues response |
| Test description 1. SUT substitutes the values of data objects in one server by another valid value of the following type: single point status double point status enumerated status integer measurand floating point measurand quality 2. SUT enables substitution 3. Force the SUT to perform a GetDataValues request on the substituted data 4. SUT disables substitution 5. Force the SUT to perform a GetDataValues request on the data that is no longer substituted |
| Comment |

| cSub3 | Substitute a value by another client | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 |
| Expected result 1. SUT displays the substituted value and quality when transmitted by the report or a GetDataValue response |
| Test description 1. Use another client to substitute a value and quality of a data object |
| Comment |

## A4.4	Block 4: Setting group selection

|  | Check that the SUT can send a correct GetLogicalNodeDirectory(SGCB) request |
| --- | --- |
|  | Verify the SUT can select a setting group (IEC 61850-7-2 clause 13 figure 18). For each setting group: SelectActiveSG of the setting group GetSGCBValues to verify active setting group |

|  | Force the SUT to perform the following requests in a way that makes the server return a response-: SelectActiveSG (IEC 61850-7-2 clause 13.3.2) GetSGCBValues (IEC 61850-7-2 clause 13.3.7) The SUT should respond to these responses as specified in the PIXIT. |
| --- | --- |

Detailed test procedures for Setting group selection

| cSg1 | Check that the SUT can send a correct GetLogicalNodeDirectory(SGCB) request | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 IEC 61850-8-1 clause 12.3.1 PIXIT |
| Expected result 1. The SUT sends a correct GetLogicalNodeDirectory(SGCB) request |
| Test description 1. Force the SUT to send a GetLogicalNodeDirectory(SGCB) request for each logical device in each server |
| Comment |

| cSg2 | Select setting group | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.3.2 IEC 61850-8-1 clause 16.2.1 PIXIT |
| Expected result 1. The SUT sends a correct SelectActiveSG request 2. The SUT sends a correct GetSGCBValues request |
| Test description 1. Force the SUT to perform a SelectActiveSG request to select first setting group of a SGCB 2. Force the SUT to perform a GetSGCBValues request to read the active setting group 3. Repeat step 1 and 2 for the other setting groups in the SGCB |
| Comment |

| cSgN1 | Pre-configured setting group deviations | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 13.3.2 IEC 61850-8-1 clause 12.3.1, 16.2.1 PIXIT |
| Expected result 1. The SUT responds as specified in PIXIT to the negative responses from the server |
| Test description 1. Force the SUT to send the following requests with invalid/non existing parameters: SelectActiveSG GetSGCBValues |
| Comment |

## A4.4+	Block 4+: Setting group definition

|  | Verify SUT can get setting group values [FC=SG] (IEC 61850-7-2 clause 13 figure 18). For each setting group: SelectActiveSG of the first setting group Use GetSGValues [FC=SG] to verify the values are of first setting group |
| --- | --- |
|  | Verify SUT can edit setting group values |

Detailed test procedures for Setting group definition

| cSg3 | Get setting group values | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.3.6 IEC 61850-8-1 clause 16.2.5 PIXIT |
| Expected result 1. SUT requests SelectActiveSG 2. SUT requests GetSGValues |
| Test description 1. Request SelectActiveSG to Select first setting group of a server 2. Request GetSGValues [FC=SG] to verify setting group values 3. Repeat for another setting group |
| Comment |

| cSg4 | Edit setting group values | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.3 IEC 61850-8-1 clause 16.2 PIXIT |
| Expected result 1. SUT requests SelectEditSG 2. SUT requests GetSGValues[FC=SE] 3. SUT requests SetSGValues[FC=SE] 4. SUT requests ConfirmEditSG |
| Test description 1. Request SelectEditSG to select first setting group of a server 2. Request GetSGValues[FC=SE] to get the current setting group values 3. Request SetSGValues[FC=SE] to set the new setting group values 4. Request ConfirmEditSG |
| Comment |

## A4.5	Block 5: Unbuffered Reporting

| Test case | Test case description |
| --- | --- |
|  | Force the SUT to perform a GetLogicalNodeDirectory(URCB) request for the logical nodes declared in the PIXIT. |
|  | SetURCBValues for RptID and DatSet.Check that the SUT overwrites mismatching RptID and DatSet values in URCBs. |
|  | Verify the client is able to process the reports with different optional fields. |
|  | Verify the client is able to process unbuffered reports with the following supported trigger conditions: on integrity on update (dupd) on update with integrity (dupd+integrity) on data change (dchg) on data and quality change (dchg+qch) On data and quality change with integrity period (dchg+qchg) |
|  | Verify the client is able to process segmented reports |
|  | Verify client can change the (pre-)configured Buffer Time (IEC 61850-7-2 clause 14.2.2.9) |
|  | Verify client can force a General interrogation |
|  | Verify that the SUT configures and enables the URCB’s as specified in the SCD file. The SUT is only allowed to write to the “dyn” URCB fields in the SCL. |
|  | Verify that the SUT can process reports with complex structured data (for example WYE and DEL data objects) |
|  | Verify that the SUT can handle reports with basic data (for example stVal and quality) |

| Test case | Test case description |
| --- | --- |
|  | Check that the SUT still communicates with other servers when it performs a GetLogicalNodeDirectory(URCB) request which returns a negative response. |
|  | Check that the SUT still works properly when it performs a GetURCBValues request which returns a negative response. |
|  | Check that the SUT still works properly when it performs a SetURCBValues request which returns a negative response. |
|  | Check that the SUT still works properly when it performs a SetURCBValues request while the URCB is reserved by another client (Resv=TRUE, PIXIT) |
|  | Check that the SUT keeps functioning normally if it receives a report that contains OptFlds that the SUT does not support. |
|  | Check that the SUT keeps functioning normally if it receives a report that contains Trigger options that the SUT does not support. |
|  | Check that the SUT behaves as described in the PIXIT when a URCB in the server has a different configuration then expected. |
|  | Verify that the SUT detects a change in the ConfRev attribute (Configuration revision, IEC 61850-7-2, 14.2.2.7) of the Report Control Block. When the SUT does not perform the ConfRev check it should check the dataset members. The means of detection need to be specified in the PIXIT. |

Detailed test procedures for Unbuffered Reporting

| cRp1 | GetLogicalNodeDirectory(URCB) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 IEC 61850-8-1 clause 12.3.1 PIXIT |
| Expected result 1. SUT correctly requests GetLogicalNodeDirectory(URCB) |
| Test description 1. Force the SUT to perform a GetLogicalNodeDirectory(URCB) |
| Comment |

| cRp2 | SetURCBValues for RptID and DatSet | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. The SUT configures the new values. |
| Test description 1. Stop SUT 2. Configure the “RptID” and the “DatSet” fields for a report control block in the SUT SCL file for one server to be different from the values in the server. 3. Configure RptID and DatSet in the ReportSettings for the server to be “Dyn” 4. Start SUT and force SUT to perform a SetURCBValues request for the mismatching RptID and DatSet |
| Comment |

| cRp3 | SUT is able to process unbuffered reports with different optional fields | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 3. The SUT sets the configured optional fields before enabling the URCB. 4. The SUT is able to process the report. |
| Test description 1. Stop SUT 2. Configure the minimum optional fields supported by the SUT for a report control block in the SUT SCL file for one server. 3. Start SUT and force SUT to enable a URCB 4. Generate a report for the configured URCB 5. Repeat step 1 to 4, this time configuring the maximum optional fields supported by the SUT in step 2 |
| Comment |

| cRp4 | SUT is able to process unbuffered reports with different trigger conditions | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. SUT is able to process the reports sent by the server. |
| Test description 1. Stop SUT 2. Configure the following (combination of) trigger conditions supported by the SUT for a URCB in the SUT SCL file for one server: integrity data update (dupd) data update and integrity (dupd+integrity) data change (dchg) data change and quality change (dchg+qchg) data change, quality change and integrity (dchg+qchg+integrity) 3. Start SUT and force SUT to enable the report URCB. 4. Force events related to the trigger conditions configured in step 2, that are related to members in the dataset of the RCB. If the trigger condition "Integrity" was configured in step 2, wait for the configured integrity period to expire. |
| Comment |

| cRp5 | SUT can process segmented unbuffered reports | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. SUT can process the reported valuechange(s) |
| Test description 1. Force a server to send a segmented, unbuffered report with a data- and/or quality-change |
| Comment |

| cRp6 | Change buffer time | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. SUT successfully sends the SetURCBValues request. |
| Test description 1. Force the SUT to perform a SetURCBValues request to change the BufTm of a URCB |
| Comment |

| cRp7 | Verify client can force a General interrogation on an unbuffered report control block | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. SUT successfully performs a general interrogation request |
| Test description 1. Force the SUT to perform a general interrogation request on a URCB |
| Comment |

| cRp8 | Enable all URCBs specified in SCL | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. The SUT configures all URCBs as specified in the SUT SCL |
| Test description 1. Force SUT to enable all URCBs that are configured in the SUT SCL |
| Comment |

| cRp9 | Verify that the SUT can process URCB reports with complex structured data | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result SUT successfully configures and enables the report control block SUT processes the report as normal |
| Test description Force SUT to Configure and enable an unbuffered report control block which contains complex structured data (e.g. WYE or DEL). Force the server to send a report for the unbuffered report control block |
| Comment |

| cRp10 | Verify that the SUT can process URCB reports with basic data | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result SUT successfully configures and enables the report control block The SUT processes the report as normal |
| Test description Force the SUT to Configure and enable an unbuffered report control block which contains basic (unstructured) data (e.g. stVal or q) Force the server to send a report for the unbuffered report control block. |
| Comment |

| cRpN1 | Renamed URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 14.2 IEC 61850-8-1 clause 12.3.1, 17.1, 17.2 PIXIT |
| Expected result 3. The SUT behaves as specified in the PIXIT |
| Test description 1. Stop a server 2. Reconfigure a URCB in the server SCL with a new valid name 3. Start server and force the SUT to perform a GetLogicalNodeDirectory(URCB) request for the LD that contains the URCB |
| Comment |

| cRpN2 | GetURCBValues.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 14.2 IEC 61850-8-1 clause 12.3.1, 17.1, 17.2 PIXIT |
| Expected result 3. SUT is able to communicate to other servers and behaves like stated in PIXIT for the server with the deleted URCB. |
| Test description 1. Stop a server 2. Remove a URCB in the server SCL 3. Start server and force the SUT to perform a GetURCBValues request for the non existing URCB |
| Comment |

| cRpN3 | SetURCBValues.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 14.2 IEC 61850-8-1 clause 12.3.1, 17.1, 17.2 PIXIT |
| Expected result 3. The SUT processes the SetURCBValues.response- as specified in the PIXIT |
| Test description 1. Stop a server 2. Change the server configuration so that one or more of the following URCB elements which where previously writable become read-only: DatSet, RptID, OptFlds, BufTm, TrgOps, IntgPd 3. Start server and force the SUT to perform a SetURCBValues request for one or more of the read-only URCB elements |
| Comment |

| cRpN4 | Report block is already reserved | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. The SUT processes the SetURCBValues.response- as specified in the PIXIT |
| Test description 1. Use another client to reserve a URCB prior to SUT and force SUT to perform a SetURCBValues request on the reserved URCB |
| Comment |

| cRpN5 | SUT is able to handle reports with unsupported optional fields | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. The SUT behaves as described in the PIXIT. 5. The SUT correctly processes the GI report. |
| Test description 1. Stop SUT 2. Configure an unbuffered report control block in the SUT SCL and the server SCL file so that it has one or more optional fields configured which are not supported by the SUT. 3. Set OptFlds in the reportsettings (for the IED containing the URCB) to conf. 4. Start SUT and force the SUT to perform a general interrogation on the URCB with unsupported optional fields 5. Force the SUT to perform a general interrogation on a URCB which is correctly configured according to the capabilities of the SUT |
| Comment |

| cRpN6 | SUT is able to handle reports with unsupported trigger conditions | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 5. The SUT behaves as described in the PIXIT. 6. The SUT correctly processes the GI report. |
| Test description 1. Stop SUT 2. Configure an unbuffered report control block in the SUT SCL and the server SCL file so that it has one or more trigger conditions configured which are not supported by the SUT. 3. Set TrgOps in the ReportSettings (for the IED containing the URCB) to conf. 4. Start SUT and force the SUT to enable the URCB with unsupported trigger conditions 5. Trigger the event(s) related to the unsupported trigger condition(s) for the server 5. Force the SUT to perform a general interrogation on a URCB which is correctly configured according to the capabilities of the SUT |
| Comment |

| cRpN7 | SUT is able to handle report control blocks with a mismatching configuration | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. The SUT behaves as described in the PIXIT. |
| Test description 1. Stop a server 2. Configure a URCB in the server SCL file in the following way: Change the referenced dataset into a new valid dataset Change the RptID Configure the dataset linked to a URCB in the server SCL file in the following way: change the order of dataset members, without changing the order of the datatypes change the order of dataset members, hereby changing the order of the datatypes remove a dataset element from the middle of the dataset add a dataset element in the middle of a dataset 3. Set DatSet and RptID in the reportsettings (for the server containing the URCB) to conf. 4. Start the server and force the SUT to enable the URCB |
| Comment |

| cRpN8 | SUT is able to detect a change in ConfRev | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 3. The SUT behaves as described in the PIXIT. |
| Test description 1. Stop a server 2. Increment the value for confRev of a URCB in the server SCL and remove a member from the referenced dataset 3. Start the server and force SUT to enable the URCB 4. Repeat step 1 to 3, this time without changing the referenced dataset in step 2 |
| Comment |

## A4.6	Block 6: Buffered Reporting

| Test case | Test case description |
| --- | --- |
|  | Force the SUT to perform a GetLogicalNodeDirectory(BRCB) request for the logical nodes declared in the PIXIT. |
|  | SetBRCBValues for RptID and DatSet. Check that the SUT overwrites mismatching RptID and DatSet values in all BRCBs.. |
|  | Verify the client is able to process the reports with different optional fields. |
|  | Verify the client is able to process buffered reports with the following supported trigger conditions: on integrity on update (dupd) on update with integrity (dupd+integrity) on data change (dchg) on data and quality change (dchg+qch) On data and quality change with integrity period (dchg+qchg) |
|  | Verify the client is able to process segmented reports |
|  | Verify client can change the (pre-)configured Buffer Time (IEC 61850-7-2 clause 14.2.2.9) |
|  | Verify client can force a General interrogation |
|  | Verify that the SUT configures and enables the BRCBs as configured in the SCD file. The SUT is only allowed to write to the “dyn” BRCB fields in the SCL. |
|  | Verify that the SUT can handle reporting of complex structured data (for example WYE and DEL data objects) |
|  | Verify that the SUT can handle reporting of basic data (for example stVal and quality) |
|  | Verify the SUT is able to process reports buffered during a lost association without bufferoverflow (PIXIT) with bufferoverflow |
|  | Verify the SUT is able to request specific buffered reports after restoring a lost association by setting the EntryID |
|  | Verify the SUT is able to purge buffered reports |

| Test case | Test case description |
| --- | --- |
|  | Check that the SUT still communicates with other servers when it performs a GetLogicalNodeDirectory (BRCB) request which returns a negative response. |
|  | Check that the SUT still works properly when it performs a GetBRCBValues request which returns a negative response. |
|  | Check that the SUT still works properly when it requests a SetBRCBValues and the response is negative. |
|  | Check that the SUT still works properly when it requests a SetBRCBValues and the BRCB is used by or pre-assigned to another client. (PIXIT) |
|  | Check that the SUT keeps functioning normally if it receives a Report which contains OptFlds that the SUT does not support. |
|  | Check that the SUT keeps functioning normally if it receives a Report which contains Trigger Options that the SUT does not support. |
|  | Mismatching reports: Report with a mismatching DataSet. Report with a mismatching RptID Report with mismatching references of the Data (when data references are enabled). Check the behaviour described in the PIXIT. |
|  | Verify that the SUT detects a change in the ConfRev attribute (Configuration revision, IEC 61850-7-2, 14.2.2.7) of the Report Control Block. When the SUT does not perform the ConfRev check it should check the dataset members. The means of detection needs to be specified in the PIXIT. |
|  | Verify the SUT can handle a severe buffer overflow with SetBRBValues(EntryID) response- |

Detailed test procedures for Buffered Reporting

| cBr1 | GetLogicalNodeDirectory(BRCB) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 IEC 61850-8-1 clause 12.3.1 PIXIT |
| Expected result 1. SUT correctly requests GetLogicalNodeDirectory(BRCB) |
| Test description 1. Force the SUT to perform a GetLogicalNodeDirectory(BRCB) |
| Comment |

| cBr2 | SetBRCBValues for RptID and DatSet | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. The SUT configures the new values. |
| Test description 1. Stop SUT 2. Configure the “RptID” and the “DatSet” fields for a report control block in the SUT SCL file for one server to be different from the values in the server. 3. Configure RptID and DatSet in the ReportSettings for the server to be “Dyn” 4. Start SUT and force SUT to perform a SetBRCBValues request for the mismatching RptID and DatSet |
| Comment |

| cBr3 | SUT is able to process buffered reports with different optional fields | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 3. The SUT sets the configured optional fields before enabling the BRCB. 4. The SUT is able to process the report. |
| Test description 1. Stop SUT 2. Configure the minimum optional fields supported by the SUT for a report control block in the SUT SCL file for one server. 3. Start SUT and force SUT to enable a BRCB 4. Generate a report for the configured BRCB 5. Repeat step 1 to 4, this time configuring the maximum optional fields supported by the SUT in step 2 |
| Comment |

| cBr4 | SUT is able to process buffered reports with different trigger conditions | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. SUT is able to process the reports sent by the server. |
| Test description 1. Stop SUT 2. Configure the following (combination of) trigger conditions supported by the SUT for a BRCB in the SUT SCL file for one server: integrity data update (dupd) data update and integrity (dupd+integrity) data change (dchg) data change and quality change (dchg+qchg) data change, quality change and integrity (dchg+qchg+integrity) 3. Start SUT and force SUT to enable the report BRCB. 4. Force events related to the trigger conditions configured in step 2, that are related to members in the dataset of the RCB. If the trigger condition "Integrity" was configured in step 2, wait for the configured integrity period to expire. |
| Comment |

| cBr5 | SUT can process segmented buffered reports | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. SUT can process the reported valuechange(s) |
| Test description 1. Force a server to send a segmented, buffered report with a data- and/or quality-change |
| Comment |

| cBr6 | Change buffer time | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. SUT successfully sends the SetBRCBValues request. |
| Test description 1. Force the SUT to perform a SetBRCBValues request to change the bufTm of a BRCB |
| Comment |

| cBr7 | Verify client can force a General interrogation on a buffered report control | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. SUT successfully performs a general interrogation request |
| Test description 1. Force the SUT to perform a general interrogation request on a BRCB |
| Comment |

| cBr8 | Enable all BRCBs specified in SCL | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. The SUT configures all BRCBs as specified in the server SCL |
| Test description 1. Force SUT to enable all BRCBs that are configured in the server SCL |
| Comment |

| cBr9 | Verify that the SUT can process BRCB reports with complex structured data | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result SUT successfully configures and enables the report control block The SUT processes the report as normal |
| Test description Force the SUT to Configure and enable a buffered report control block which contains complex structured data. (e.g. WYE or DEL) Force the server to send a report for the buffered report control block |
| Comment |

| cBr10 | Verify that the SUT can process BRCB reports with basic data | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result SUT successfully configures and enables the report control block The SUT processes the report as normal |
| Test description Force the SUT to Configure and enable a buffered report control block which contains basic (unstructured) data (e.g. stVal or q) Force the server to send a report for the buffered report control block |
| Comment |

| cBr11 | Process buffered reports with and without buffer overflow | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 5. The SUT handles the buffered reports 8. The SUT handles the buffered reports as specified in PIXIT |
| Test description 1. Configure and enable a BRCB with trigger conditions data change and all supported optional fields. 2. Force data changes in a server to force reports 3. Disconnect the Ethernet cable between the server and switch 4. Force data changes in the server to force report buffering 5. Restore the Ethernet connection 6. Disconnect the Ethernet cable between the server and switch 7. Force many data changes in the server to force buffer overflow 8. Restore the Ethernet connection |
| Comment |

| cBr12 | Set EntryId of buffered reports | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 5. The SUT is able to process the buffered reports |
| Test description 1. Configure and enable a BRCB with trigger conditions data change and/or quality change, and all supported optional fields. 2. Force data/quality changes in a server to force reports 3. Disconnect the Ethernet cable between switch and the server 4. Force data/quality changes in the server to force buffered reports 5. Restore the Ethernet connection 6. Force SUT to send a correct SetBRCBValues request for the EntryID that was last received by the SUT |
| Comment |

| cBr13 | Purge buffered reports | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 6. The SUT requests purge buffer |
| Test description 1. Configure and enable a BRCB with trigger conditions data change and/or quality change, and all supported optional fields. 2. Force data/quality changes in a server to force reports 3. Disconnect the Ethernet cable between switch and the server 4. Force data/quality changes in the server to force buffered reports 5. Restore the Ethernet connection 6. Force SUT to purge buffered reports (PIXIT) |
| Comment |

| cBrN1 | Renamed BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 14.2 IEC 61850-8-1 clause 12.3.1, 17.1, 17.2 PIXIT |
| Expected result 3. The SUT behaves as specified in the PIXIT |
| Test description 1. Stop a server 2. Reconfigure a BRCB in the server SCL with a new valid name 3. Start server and force the SUT to perform a GetLogicalNodeDirectory(BRCB) request for the LD which contains the BRCB |
| Comment |

| cBrN2 | GetBRCBValues.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 14.2 IEC 61850-8-1 clause 12.3.1, 17.1, 17.2 PIXIT |
| Expected result 3. SUT is able to communicate to other servers and behaves like stated in PIXIT for the server with the deleted BRCB. |
| Test description 1. Stop a server 2. Remove a BRCB in the server SCL 3. Start server and force the SUT to perform a GetBRCBValues request for the non existing BRCB |
| Comment |

| cBrN3 | SetBRCBValues.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 14.2 IEC 61850-8-1 clause 12.3.1, 17.1, 17.2 PIXIT |
| Expected result 3. The SUT processes the SetBRCBValues.response- as specified in the PIXIT |
| Test description 1. Stop a server 2. Change the server configuration so that one or more of the following BRCB elements which where previously writable become read-only: DatSet, RptID, OptFlds, BufTm, TrgOps, IntgPd 3. Start server and force the SUT to perform a SetBRCBValues request for one or more of the read-only BRCB elements |
| Comment |

| cBrN4 | Report block is already reserved | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 1. The SUT behaves as specified in the PIXIT |
| Test description 1. Use another client to enable a BRCB prior to SUT and force SUT to perform a SetBRCBValues request on the BRCB |
| Comment |

| cBrN5 | SUT is able to handle reports with unsupported optional fields | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. The SUT behaves as described in the PIXIT. 5. The SUT correctly processes the GI report. |
| Test description 1. Stop SUT 2. Configure a buffered report control block in the SUT SCL and the server SCL file so that it has one or more optional fields configured which are not supported by the SUT. 3. Set OptFlds in the reportsettings (for the IED containing the BRCB) to conf. 4. Start SUT and force the SUT to perform a general interrogation on the BRCB with unsupported optional fields 5. Force the SUT to perform a general interrogation on a BRCB which is correctly configured according to the capabilities of the SUT |
| Comment |

| cBrN6 | SUT is able to handle reports with unsupported trigger conditions | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 5. The SUT behaves as described in the PIXIT. 6. The SUT correctly processes the GI report. |
| Test description 1. Stop SUT 2. Configure a buffered report control block in the SUT SCL and the server SCL file so that it has one or more trigger conditions configured which are not supported by the SUT. 3. Set TrgOps in the reportsettings (for the IED containing the BRCB) to conf. 4. Start SUT and force the SUT to enable the BRCB with unsupported trigger conditions 5. Trigger the event(s) related to the unsupported trigger condition(s) for the server 5. Force the SUT to perform a general interrogation on a BRCB which is correctly configured according to the capabilities of the SUT |
| Comment |

| cBrN7 | SUT is able to handle report control blocks with a mismatching configuration | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 4. The SUT behaves as described in the PIXIT. |
| Test description 1. Stop a server 2. Configure a BRCB in the server SCL file in the following way: Change the referenced dataset into a new valid dataset Change the RptID Configure the dataset linked to a BRCB in the server SCL file in the following way: change the order of dataset members, without changing the order of the datatypes change the order of dataset members, hereby changing the order of the datatypes remove a dataset element from the middle of the dataset add a dataset element in the middle of a dataset 3. Set DatSet and RptID in the ReportSettings (for the server containing the BRCB) to conf. 4. Start the server and force the SUT to enable the BRCB |
| Comment |

| cBrN8 | SUT is able to detect a change in ConfRev | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 3. The SUT behaves as described in the PIXIT. |
| Test description 1. Stop a server 2. Increment the value for confRev of a BRCB in the server SCL and remove a member from the referenced dataset 3. Start the server and force SUT to enable the BRCB 4. Repeat step 1 to 3, this time without changing the referenced dataset in step 2 |
| Comment |

| cBrN9 | Set non-existing EntryID | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.1, 17.2 PIXIT |
| Expected result 5. The SUT will behave as specified in PIXIT |
| Test description 1. Force data changes in a server to force reports 2. Disconnect the Ethernet cable between the Ethernet switch and the server 3. Force many data changes in a server to force a buffer overflow Restore the Ethernet connection Force SUT to perform a SetBRCBValues request with an EntryID from a discarded report |
| Comment |

## A4.7	Block 7: Logging

| Test case | Test case description |
| --- | --- |
|  | Check if the SUT is able to request a GetLogicalNodeDirectory (LOG) of the logical nodes declared in the PIXIT of all configured servers. |
|  | Check if the SUT is able to request a GetLogicalNodeDirectory(LCB) of the logical nodes declared in the PIXIT of all configured servers. |
|  | Check if the SUT is able to request a GeLogStatusValues of the LOGs found with the GetLogicalNodeDirectory(LCB) services |
|  | Check if the SUT is able to request a GeLCBValues of the LCBs found with the GetLogicalNodeDirectory(LCB) services |
|  | If the SUT configures the server’s LogControlBlock parameters after start-up using SetLCBValues, check that the SetLCBValues are sent with the configured values. |
|  | Force the SUT to enable the Logging of at least one LOG of the server and check the client send the request correctly. |
|  | Force the SUT to QueryLogByTime or QueryLogByEntry and check the SUT updates its database with the Log entries received. |

| Test case | Test case description |
| --- | --- |
|  | Check that the SUT still communicates with other servers when it request GetLogicalNodeDirectory (LCB) and GetLogicalNodeDirectory (LOG) with negative response. |
|  | Check that the SUT still works properly when it requests a GetLCBValues/GetLogStatusValues when the response is negative. |
|  | Check that the SUT still works properly when it requests a SetLCBValues when the response is negative. |

The detailed test procedures need to be defined.

## A4.12	Block 12: Control

| Test case | Test case description |
| --- | --- |
|  | Check if the SUT is able to set the TEST field in the commands (PIXIT). |
|  | Check if the SUT is able to set the following (combination of) CHECK bits in the commands (PIXIT) for the supported control models: Synchro Check Interlock Check Synchro Check and Interlock Check |
|  | Check if the SUT is able to change control model using online services (PIXIT). |
|  | Verify the values of originator category, origin identification and the control number (PIXIT) |

| Test case | Test case description |
| --- | --- |
|  | Check if the SUT reacts as described in the PIXIT when it detects a control model mismatch: Server status-only, SUT expects controllable Server SBO, SUT expects direct operate Server direct operate, SUT expects SBO Server SBO enhanced SUT expects SBO normal |
|  | Check if the SUT reacts as described in the PIXIT when it detects a control model that is not initialized in the SCL file |

The testing of the control model has been divided in the four possible control models that can be implemented:

- Direct control with normal security.

- SBO control with normal security.

- Direct control with enhanced security.

- SBO control with enhanced security.

Detailed test procedures for Control

| cCtl1 | Test mode | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.5.2.4 IEC 61850-8-1 clause 20, Annex E |
| Expected result DO normal/enhanced security: The SUT sends the Operate request with Test flag = true SBO normal security: The SUT sends the Operate requests with Test flag = true SBO enhanced security: The SUT sends the SelectWithValue and Operate requests with Test flag = true |
| Test description DO normal/enhanced security: Force the SUT to perform an Operate request with the Test flag set SBO normal security: Force the SUT to perform a Select request followed by an Operate request with the Test flag set SBO enhanced security: Force the SUT to perform a SelectWithValue request followed by an Operate request, both with the Test flag set |
| Comment |

| cCtl2 | Synchro and interlock check | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.5.2.5 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result The SUT sends the request(s) with the Check bits as specified in PIXIT. |
| Test description DO normal/enhanced security: Force the SUT to send an Operate request with the Synchro Check bit set Force the SUT to send an Operate request with the Interlock Check bit set Force the SUT to send an Operate request with the Interlock and Synchro Check bit set SBO normal security: Force the SUT to perform a Select and Operate request with the Synchro Check bit set Force the SUT to perform a Select and Operate request with the Interlock Check bit set Force the SUT to perform a Select and Operate request with the Interlock and Synchro Check bit set SBO enhanced security: Force the SUT to perform a SelectWithValue and Operate request, both with the Synchro Check bit set Force the SUT to perform a SelectWithValue and Operate request, both with the Interlock Check bit set Force the SUT to perform a SelectWithValue and Operate request, both with the Interlock and the Synchro Check bit set |
| Comment |

| cCtl3 | Change control model | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2, 17.3 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result The SUT sends the SetDataValues request with the corresponding control model |
| Test description Force the SUT to perform a SetDataValues request to change control model to “Direct control with normal security” Force the SUT to perform a SetDataValues request to change control model to “SBO control with normal security” Force the SUT to perform a SetDataValues request to change control model to “Direct control with enhanced security” Force the SUT to perform a SetDataValues request to change control model to “SBO control with enhanced security” |
| Comment |

| cCtl4 | Verify control number and originator | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2, 17.3 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result The SUT sets the control number and the originator as specified in PIXIT |
| Test description Execute the applicable control model specific test cases |
| Comment this is a continuous effort during the conformance test of the supported control models |

| cCtlN1 | Control model deviations | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2, 17.3 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result 4. The SUT responds as specified in the PIXIT |
| Test description 1. Stop a server 2. Reconfigure the server: Reconfigure one controllable object to status only Reconfigure one SBO object to direct operate Reconfigure one direct object to SBO Reconfigure SBO enhanced security control object to SBO normal security Start server Force the SUT to perform a Select/Operate request for the reconfigured control object |
| Comment |

| cCtlN2 | Control model not configured in SCL | Out of scope |
| --- | --- | --- |
| Expected result |
| Test description |
| Comment Testcase is out of scope for IEC 61850 |

## A4.12a	Block 12a: Direct Control

| Test case | Test case description |
| --- | --- |
|  | OperReq[test ok] resp+ Perform a correct Operate request. Check that the SUT does not generate an error. |
|  | OperReq[test not ok] resp- Client requests Oper resulting in Test not ok. Check that the SUT realizes the operation failed. |
|  | TimOperReq[test not ok] resp- Client requests TimOper resulting in Test not ok. Check that the SUT realizes the time operation failed. |
|  | TimOperReq[test ok] + TimerExpired[test ok] resp+ Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test Ok'. Verify the WaitForActionTime results in a timer expired ‘Test ok’ and that the SUT realizes the operation succeeded. |
|  | TimOperReq[test ok] + TimerExpired[test not ok] resp- Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test Ok'. Force situation that the WaitForActionTime results in a timer expired ‘Test not ok’. Check that the SUT realizes the operation failed. |

Detailed test procedures for Direct Control with normal security (DOns), excluding TimeActivatedOperate test cases.

| cDOns1 | Successful Operate | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.1 IEC 61850-8-1 clause 20.7 |
| Expected result 1. The SUT processes the response |
| Test description 1. Force the SUT to perform an Operate request on a DOns control object |
| Comment |

| cDOns2 | Failed Operate | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.1 IEC 61850-8-1 clause 20.7 |
| Expected result 1. The SUT processes the response- as specified in the PIXIT |
| Test description 1. Force the SUT to perform an Operate request on a DOns control object that results in a Operate.response- with a Last Application Error (Tissue #246) |
| Comment |

## A4.12b	Block 12b: SBO Control

| Test case | Test case description |
| --- | --- |
|  | SelectReq[test not ok] resp-: Force the SUT to perform a Select request that results in Test not ok. Check that the SUT handles the Select.response- as specified in the PIXIT. |
|  | SelectReq[test ok] resp+ and OperReq[test ok] resp+ of selected object Force the SUT to send a Select request for an SBOns object. Force the SUT to perform a correct Operate request. Check that the SUT sends correct Select and Operate requests. |
|  | SelectReq[test ok] resp+ and OperReq[test not ok] resp- of selected object. Force the SUT to perform a correct Select request, followed by an Operate request that results in Test not ok. Check that the SUT is able to process the Operate.response- |
|  | SelectReq[test ok] resp+ and CancelReq of selected object. Check that the SUT can send a correct Cancel request. |
|  | SelectReq[test ok] resp+ and TimOperReq[test ok] resp+ of selected object Check that the SUT is able to send a correct TimeActivated Operate request and that the SUT is able to process the response. |
|  | SelectReq[test ok] resp+ and TimOperReq[test not ok] resp- of selected object Check that the SUT can process a Operate.response- |

Detailed test procedures for SBO Control with normal security (SBOns), excluding TimeActivatedOperate test cases.

| cSBOns1 | Failed Select | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2, 17.5.3.2 IEC 61850-8-1 clause 20.4 PIXIT |
| Expected result 3. The SUT handles the Select.response- as described in the PIXIT |
| Test description 1. Force the SUT to perform a correct Select request for which the server sends a response- |
| Comment |

| cSBOns2 | Select and successful Operate | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2, 17.5.3.5 IEC 61850-8-1 clause 20.7 |
| Expected result 1. The SUT sends a correct Select request for the SBOns object 2. The SUT sends a correct Operate request on the selected SBOns object |
| Test description 1. Force the SUT to perform a Select request on an SBOns object 2. Force the SUT to perform an Operate request on the selected SBOns object |
| Comment |

| cSBOns3 | Select and failed Operate | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2, 17.5.3.5 IEC 61850-8-1 clause 20.7 |
| Expected result 5. SUT indicates Operate failure |
| Test description 1. Force the SUT to send a correct Select request 2. Force the SUT to perform an Operate request that results in an Operate.response- with a Last Application error (Tissue #246) |
| Comment |

| cSBOns4 | Cancel | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2, 17.5.3.4 IEC 61850-8-1 clause 20.6 |
| Expected result 1. The SUT sends a correct Select request 2. The SUT sends a correct Cancel request |
| Test description 1. Force the SUT to perform a Select request for an SBOns object 2. Force the SUT to perform a Cancel request on the selected object |
| Comment |

## A4.12c	Block 12c: Direct Control with Enhanced Security

| Test case | Test case description |
| --- | --- |
|  | OperReq[test ok] resp+: Force the SUT to send a correct Operate request that causes the server to send an Operate.response+ and: a CommandTermination+. a CommandTermination- (PIXIT) Check that the SUT processes the CommandTermination+ and the CommandTermination- as specified in the PIXIT |
|  | OperReq[test not ok] resp-: Check that the SUT behaves as specified in the PIXIT when it receives an Operate.response- |
|  | TimOperReq[test not ok] resp-: Check that the SUT behaves as described in the PIXIT when it receives a Operate.response- |
|  | TimOperReq[test ok] resp+: Force the SUT to send a correct TimeActivated Operate request that causes the server to send a Operate.response+ and: a CommandTermination+ a CommandTermination- Check that the SUT can process the CommandTermination+ and the CommandTermination- |

Detailed test procedures for Direct Control with enhanced security (DOes), excluding TimeActivatedOperate test cases.

| cDOes1 | Successful Operate with command termination | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.2, 17.5.3.5 IEC 61850-8-1 clause 20.7 and 20.8 PIXIT |
| Expected result 1. Check that the SUT processes the Command termination as specified in the PIXIT |
| Test description Force the SUT to send a correct Operate request that causes the server to send an Operate.response+ and: a CommandTermination+ a CommandTermination- |
| Comment |

| cDOes2 | Operate failure | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.2, 17.5.3.5 IEC 61850-8-1 clause 20.7 and 20.8 PIXIT |
| Expected result 1. The SUT processes the Operate.response- as specified in the PIXIT |
| Test description 1. Force the SUT to perform an Operate that results in an Operate.response- |
| Comment |

## A4.12d	Block 12d: Enhanced SBO Control

| Test case | Test case description |
| --- | --- |
|  | SelectWithValue [test not ok] resp-: Force the SUT to perform a SelectWithValue request that results in a test not ok. |
|  | SelectWithValue [test ok] resp+ and OperReq[test ok] resp+ of selected object Force the SUT to send a correct SelectWithValue request, followed by a correct Operate request. |
|  | SelectWithValue [test ok] resp+ and OperReq[test not ok] resp- of selected object. Force the SUT to send a correct SelectWithValue request, followed by an Operate request that results in test not ok. Check that the SUT behaves as described in the PIXIT when it recieves the Operate.response- |
|  | SelectWithValue [test ok] resp+ and CancelReq of selected object. Force the SUT to send a correct SelectWithValue request, followed by a correct Cancel request. |
|  | SelectWithValue [test ok] resp+ and TimOperReq[test ok] resp+ of selected object Force the SUT to perform a correct SelectWithValue request, followed by a correct TimeActivedOperare request. Check that the SUT processes the response as specified in the PIXIT. |
|  | SelectWithValue [test ok] resp+ and TimOperReq[test ok] resp- of selected object Force the SUT to perform a correct SelectWithValue request, followed by a TimeActivedOperate request that results response-.. |

Detailed test procedures for SBO Control with enhanced security (SBOes), excluding TimeActivatedOperate test cases.

| cSBOes1 | SelectWithValue – test not ok | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3, 17.5.3.3 IEC 61850-8-1 clause 20.5, 20.8 |
| Expected result 2. SUT indicates SelectWithValue failure |
| Test description 1. Force the SUT to perform a SelectWithValue request that results in a SelectWithValue.response- |
| Comment |

| cSBOes2 | SelectWithValue and successfull Operate | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3, 17.5.3.5 IEC 61850-8-1 clause 20.5, 20.7, 20.8 |
| Expected result 1. The SUT performs a correct SelectWithValue request 2. The SUT performs a correct Operate request |
| Test description 1. Force the SUT to perform a SelectWithValue request for an SBOes object 2. Force the SUT to perform an Operate request for the selected object |
| Comment |

| cSBOes3 | SelectWithValue and failed Operate | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3, 17.5.3.5 IEC 61850-8-1 clause 20.5, 20.7, 20.8 |
| Expected result 1. The SUT performs a correct SelectWithValue request 2. The SUT performs a correct Operate request |
| Test description 1. Force the SUT to perform a SelectWithValue request 2. Force the SUT to perform an Operate request that results in an Operate.response- |
| Comment |

| cSBOes4 | Cancel | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3, 17.5.3.4 IEC 61850-8-1 clause 20.6, 20.8 |
| Expected result 1. The SUT performs a correct SelectWithValue request 2. The SUT performs a correct Cancel request |
| Test description 1. Force the SUT to perform a SelectWithValue request 2. Force the SUT to perform a Cancel request |
| Comment |

## A4.13	Block 13: Time and time synchronization

|  | Verify that the SUT supports the SCSM time synchronisation, Change the time in the time server and verify the SUT uses the new time |
| --- | --- |
|  | Check that the timestamp accuracy of the SUT matches the documented timestamp accuracy. |

|  | Verify that a lost time synchronisation is detected after a specified period and the timestamp quality invalid is set |
| --- | --- |
|  | Verify the SUT handles the time stamp quality coming from the time server |

Detailed test procedures for Time and time synchronization

| cTm1 | Time synchronisation | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result 3. The SUT uses the new timestamp |
| Test description 1. SUT exposes the time and time quality as specified in the PIXIT 2. Test engineer changes the time of the time server and waits till SUT has received the new time synch message 3. SUT exposes the time and time quality as specified in the PIXIT |
| Comment |

| cTm2 | Time accuracy | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result 1. SUT timestamp accuracy matches with the documented accuracy 3. SUT uses the new timestamp |
| Test description 1. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp 2. Test engineer changes the time of the time server and waits till SUT has received the new time synch message 3. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp |
| Comment |

| cTmN1 | Time synchronisation lost | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21, PIXIT |
| Expected result 1. SUT uses the correct timestamp 3. SUT uses the timestamp with “ClockNotsynchronized” 5. SUT uses the correct timestamp |
| Test description 1. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp 2. Test engineer stops or disconnects the time server and waits for the SUT to detect the time server is lost 3. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp 4. Test engineer restarts or reconnects the time server and waits till SUT has received the time synch message 5. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp |
| Comment |

| cTmN2 | Time synchronisation with ClockFailure from time server | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21, PIXIT |
| Expected result 1. SUT uses the correct timestamp and quality 3. SUT uses the timestamp quality with “ClockFailure” |
| Test description 1. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp 2. Test engineer forces “ClockFailure” in SNTP time server 3. SUT displays the time and time quality (PIXIT) or requests a service including the timestamp |
| Comment |

## A4.14	Block 14: File transfer

|  | Verify that the SUT can send a GetServerDirectory(FILE) request with correct parameters and that the SUT is able to process the response (IEC 61850-7-2 clause 6.2.2) |
| --- | --- |
|  | Verify that the SUT can send a GetFileAttributeValues request with correct parameters and verify that the SUT is able to process the response (IEC 61850-7-2 clause 20.2.4) |
|  | Verify that the SUT can send a GetFile request with correct parameters and verify the SUT handles the response (IEC 61850-7-2 clause 20.2.1) |
|  | Verify that the SUT can perform a SetFile request with correct parameters and handles the response (IEC 61850-7-2 clause 6.2.2) |
|  | Verify that the SUT can send a DeleteFile request with correct parameters and verify that the SUT can process the response |

| cFtN1 | Verify that the SUT is able to process a GetFile.response- |
| --- | --- |
| cFtN2 | Verify that the SUT is able to process a GetFileAttributeValues.response- |
| cFtN3 | Force the SUT to perform a SetFile request that results in a SetFile.response-. Check that the SUT processes the response as specified in the PIXIT. |

Detailed test procedures for File transfer

| cFt1 | GetServerDirectory(FILE) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 6.2.2 IEC 61850-8-1 clause 9.3, 23.2 PIXIT |
| Expected result 1. The SUT processes the GetServerDirectory response |
| Test description 1. Force the SUT to perform a GetServerDirectory(FILE) request with and without folder name |
| Comment GetServerDirectory(FILE) and GetFileAttributeValues are mapped on the same MMS service |

| cFt2 | GetFileAttributeValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 6.2.2 IEC 61850-8-1 clause 9.3, 23.2 PIXIT |
| Expected result 1. The SUT processes the GetFileAttributeValues response |
| Test description 1. Force the SUT to perform a GetFileAttributeValues request with and without folder name |
| Comment GetServerDirectory(FILE) and GetFileAttributeValues are mapped on the same MMS service |

| cFt3 | GetFile | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.1 IEC 61850-8-1 clause 23.2.1 PIXIT: file size 0 |
| Expected result 1. The SUT processes the file 2. The SUT processes the file 3. The SUT processes the file |
| Test description 1. Force the SUT to perform a GetFile request for a small file of about 1kB 2. Force the SUT to perform a GetFile request for a file with file size 0 (unknown) 3. Force the SUT to perform a GetFile request for a large file of about 1MB |
| Comment |

| cFt4 | SetFile | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.2 IEC 61850-8-1 clause 23.2.2 PIXIT |
| Expected result 1. The SUT performs a correct SetFile request and sends the file to the server 2. The SUT performs a correct SetFile request and sends the file to the server |
| Test description 1. Force the SUT to perform a SetFile request with a small file of about 1kB 2. Force the SUT to perform a SetFile request with a large file of about 1MB |
| Comment |

| cFt5 | DeleteFile | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.2 IEC 61850-8-1 clause 23.2.3 |
| Expected result 1. The SUT sends a correct DeleteFile request |
| Test description 1. Force the SUT to perform a DeleteFile request on an existing, deletable file |
| Comment |

| cFtN1 | GetFile.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.1 IEC 61850-8-1 clause 23.2.1 PIXIT |
| Expected result 1. The SUT processes the GetFile.response- |
| Test description 1. Force the SUT to perform a GetFile request that results in a GetFile.response- |
| Comment |

| cFtN2 | GetFileAttributeValues.response- | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.4 IEC 61850-8-1 clause 23.2.4 PIXIT |
| Expected result 1. The SUT processes the GetFileAttributeValues.response- |
| Test description 1. Force the SUT to perform a GetFileAttributeValues request that results is a GetFileAttributeValues.response- |
| Comment |

| cFtN3 | SetFile response- |  |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.2 IEC 61850-8-1 clause 23.2.2 |
| Expected result 1. The SUT processes the SetFile.response- |
| Test description 1. Force the SUT to perform a SetFile request that results in a SetFile.response- |
| Comment |

A5	Mapping on GOOSE (IEC 61850-7-2 and IEC 61850-8-1)

The test procedures are structured according to conformance blocks. The following table specifies which ACSI services, mapped on GOOSE, are mandatory/optional for IEC 61850-8-1 Client systems.

Table A.5.1: ACSI services per conformance block for IEC 61850-8-1 Client systems

| Conformance Block | Mandatory | Optional |
| --- | --- | --- |
| 9b: GOOSE subscribe | SendGOOSEMessage (subscribe) | GetLogicalNodeDirectory (GoCB) GetGoCBValues SetGoCBValues |

The following table specifies which test procedures are mandatory/conditional for each conformance block. Conditions refer to the SCL - IED - Services section, the PICS or PIXIT.

Table A.5.2: Test procedures per conformance block

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 9b: GOOSE subscribe | cGos1, cGos2, cGos3, cGosN1, cGosN2, cGosN3, cGosN4, cGosN5, cGosN6 |  |

Note: Get/SetGoCBValues test procedures are not available yet

The following paragraphs describe the abstract test cases and the corresponding detailed test procedure.

## A5.9b	Block 9b: GOOSE subscribe

Both the IEC 61850 client and server can behave as a GOOSE subscriber. The abstract GOOSE subscribe test cases defined for the server are copied for the client. The detailed test procedures will be different.

|  | Send single GOOSE message with/without the VLAN tag with new data and check if the message is received and the data has the new value by e.g. check binary output, event list, logging or MMI |
| --- | --- |
|  | Send single GOOSE message with the Test or ndsCom parameter set. Verify that on a status change the values are not used for operational purposes (IEC 61850-7-2 clause 15.2.3.8) |
|  | Proper detection and action roll-over of sqNum with no status change (sqNum=max -> sqNum = 1) and with status change (sqNum=max -> sqNum = 0) |

|  | Check behaviour of SUT as specified in PIXIT on Missing GOOSE message |
| --- | --- |
|  | Check behaviour of SUT as specified in PIXIT on Double GOOSE message |
|  | Check behaviour of SUT as specified in PIXIT on Delayed GOOSE message, with and without exceeding timeAllowedToLive |
|  | Check behaviour of SUT as specified in PIXIT on Out of order GOOSE message |
|  | Check behaviour of SUT as specified in PIXIT on No GOOSE messages |
|  | Check behaviour of SUT as specified in PIXIT on invalid GOOSE messages gocbRef different from GoCB and NULL timeAllowedtoLive = 0 DatSet different from GoCB and NULL goID different from GoCB and NULL t contains the time of a status change minus/plus one hour confRev different from GoCB and NULL numDatSetEntries 0, more, less with the number of data entries in the allData allData values do not match with the DatSet element type APPID different from SCL and 0 (IEC 61850-8-1 Annex C) |

The detailed test procedures need to be defined.

A6	Free form testing

For free form testing a test lab can add extra test cases/procedures and propose these to the UCA IUG. The UCA IUG decides if and how to include the test case in the next revision.

# Annex B – Detailed description of test results

This appendix contains detailed comments on test results, for instance when a defect is detected or to explain an inconclusive test result, including the actual message flow if appropriate.

<Test procedure identifier X>

<Additional extra information, e.g. a trace dump>

# Annex C – PIXIT Template for Client

Introduction

This document specifies the protocol implementation extra information for testing (PIXIT) of the IEC 61850 interface in the client system:  “<product>” with version “<version>”, further referred to as “client”.

Together with the PICS and the MICS the PIXIT forms the basis for a conformance test according to IEC 61850-10.

The following chapters specify the PIXIT for each applicable ACSI service model as structured in IEC 61850-10 and the “Conformance Test Procedures for Client System with IEC 61850-8-1 interface”.

PIXIT for Configuration

| Description | Value / Clarification |
| --- | --- |
| Describe how the client handles nameplate configuration revision mismatches |  |
| Describe how the client handles report control block configuration revision mismatches |  |
| <additional items> |  |

PIXIT for Association model

| Description | Value / Clarification |
| --- | --- |
| Guaranteed number of servers that can set-up an association simultaneously (one association per server) |  |
| Lost connection detection time range (default range of TCP_KEEPALIVE is 1 – 20 seconds) | … seconds |
| Lost (abort) connection retry time | … seconds |
| Is authentication supported | Y/N |
| What is the maximum and minimum MMS PDU size | Max MMS PDU size Min MMS PDU size |
| What is the typical startup time after a power supply interrupt |  |
| How does the client behave in case of a lost connection with (one of) the associated servers? |  |
| How does the client behave when a server denies an Association request by the client? |  |
| Does the client automatically reconnect to the configured servers after startup (Automatic statup)? | Y/N |
| <additional items> |  |

PIXIT for Server model

| Description | Value / Clarification |
| --- | --- |
| Maximum object identification length | 129 octects: <64>/<64> |
| Does client support autodescription | <describe the autodescription procedure> |
| What analogue value (MX) quality bits are used in the client | Y/N Good, Y/N Invalid, Y/N Reserved, Y/N Questionable Y/N Overflow Y/N OutofRange Y/N BadReference Y/N Oscillatory Y/N Failure Y/N OldData Y/N Inconsistent Y/N Inaccurate Y/N Process Y/N Substituted Y/N Test Y/N OperatorBlocked |
| Which status value (ST) quality bits are used in the client | Y/N Good, Y/N Invalid, Y/N Reserved, Y/N Questionable Y/N BadReference Y/N Oscillatory Y/N Failure Y/N OldData Y/N Inconsistent Y/N Inaccurate Y/N Process Y/N Substituted Y/N Test Y/N OperatorBlocked |
| Describe how to view/display quality values |  |
| Describe how to force a SetDataValues request |  |
| Describe how to force a GetAllDataValues request |  |
| Describe how the client behaves in case of: GetDataDefinition response- GetLogicalDeviceDirectory response- GetAllDataValues response- GetDataValues response- SetDataValues response- |  |

PIXIT for Data set model

| Description | Value / Clarification |
| --- | --- |
| Describe how to force a GetDataSetValues request |  |
| Describe how to force a SetDataSetValues request |  |
| Describe how to force a DeletaDataSet request |  |
| Describe how the client handles following dataset mismatches between the SCL and the data sets exposed via MMS: new dataset element missing dataset element Reordered dataset members in a dataset of a different data type Reordered dataset members in a dataset of the same data type |  |
| Describe how the client behaves in case of: GetLogicalNodeDirectory(DATA-SET) response- GetDataSetDirectory response- |  |
| Does the client support the creation of: persistent datasets non-persistent datasets | Y/N Y/N |
| Describe how the client behaves in case of: CreateDataSetDirectory response- DeleteDataSet response- |  |
| Describe how the client behaves when it receives a SetDataSetValues.Response- |  |
| <additional items> |  |

PIXIT for Substitution model

| Description | Value / Clarification |
| --- | --- |
| Describe how to substitute a value |  |
| <additional items> |  |

PIXIT for Setting group control model

| Description | Value / Clarification |
| --- | --- |
| Describe how to change the active setting group |  |
| Describe how to get the actual setting group values |  |
| Describe how to edit setting group values |  |
| Describe how the client behaves in case of: GetSGCBValues response- The configured SG is different then the actual setting group |  |
| <additional items> |  |

PIXIT for Reporting model

| Description | Value / Clarification |
| --- | --- |
| Does the client search for RCB in all logical nodes? when not specify the logical nodes | All logical nodes or The following logical nodes: |
| Which dynamic RCB attributes are/can be configured by the client | RptID Y/N DataSet Y/N Optional fields Y/N Trigger conditions Y/N Buffer time Y/N Integrity period Y/N |
| Does the client supports IEDs with indexed and non-indexed report control blocks (RCB) | Buffered RCB indexed Y/N Buffered RCB not indexed Y/N Unbuffered RCB indexed Y/N Unbuffered RCB not indexed Y/N |
| The supported trigger conditions are | integrity Y/N data change Y/N quality change Y/N data update Y/N general interrogation Y/N |
| The supported optional fields are | sequence-number Y/N report-time-stamp Y/N reason-for-inclusion Y/N data-set-name Y/N data-reference Y/N buffer-overflow Y/N entryID Y/N conf-rev Y/N |
| The minimum required optional fields are | sequence-number Y/N report-time-stamp Y/N reason-for-inclusion Y/N data-set-name Y/N data-reference Y/N buffer-overflow Y/N entryID Y/N conf-rev Y/N |
| Does the client support segmented reports | Y/N |
| Does the client support pre-assigned RCB | Y/N |
| Does the client support indexed RCBs | Y/N |
| Does the client support reported data set containing structured data objects or data attributes? | reporting of data objects Y/N reporting of data attributes Y/N |
| Describe how the client does respond when an URCB is already reserved |  |
| Describe how the client does respond when a BRCB is already reserved |  |
| Describe how the client does respond on a SetBRCBValues(EntryID) respond- |  |
| Describe how the client does respond when a report has an unknown: dataset, RptID, unexpected number of dataset entries, and/or unexpected data type format entries |  |
| Describe how the client detects reporting configuration changes (mismatches). Does it check the “configuration revision” attributes and/or does it check the dataset members? |  |
| Describe how to force the client to change the RCB BufTm |  |
| Describe how the client behaves when it receives a report that has the buffer overflow flag set? |  |
| Describe how to force the client to write a (valid) EntryID value. |  |
| Describe how to force the client to purge the report buffer. |  |
| Describe how the client responds when it receives a GetXRCBValues.response- |  |
| Describe how the client responds when it receives a SetXRCBValues.response- |  |
| Describe how the client responds when it tries to use a RCB that is reserved by another client |  |
| Describe how the client behaves when it receives a report that contains optional fields that are not supported by the client |  |
| Describe how the client behaves when it receives a report that was caused by one or more trigger conditions that are not supported by the client |  |
| Describe how the client behaves when it encounters an RCB with a different dataset configuration than expected. |  |
| Describe how the client behaves when it encounters an RCB with a different confRev value than expected |  |
| Describe how the client responds when it sets an EntryID value that is not recognized by the server. |  |
| Is there a maximum number of report control blocks that the client can enable? | No, there is no known maximum / Yes, the maximum number of report control blocks that can be enabled per server by the client is … |
| <additional items> |  |

PIXIT for Logging model

| Description | Value / Clarification |
| --- | --- |
| Does the client search for LCB in all logical nodes? when not specify the logical nodes | All logical nodes or The following logical nodes: |
| Describe how to change LOG and LCB attributes |  |
| <additional items> |  |

PIXIT for Generic substation events model

| Description | Value / Clarification |
| --- | --- |
| What elements of a subscribed GOOSE header are checked to decide the message is valid and the allData values are accepted? Ignored = element value is not checked, message will be accepted SCL match = element value should match with the configuration, otherwise the GOOSE message will be ignored | N source MAC address = ignored Y dest. MAC address = SCL match N VLAN id = ignored N VLAN priority = ignored Y Ethertype = 0x88B8 Y/N gocbRef = SCL match Y/N timeAllowedtoLive = see below Y/N DatSet = SCL match Y/N goID = SCL match N t = ignored Y/N stNum = <describe> Y/N sqNum = see below Y/N test = false (true will be ignored) Y/N confRev = SCL match Y/N ndsCom = false (true will be ignored) Y/N numDatSetEntries = SCL match |
| For the checked GOOSE header elements describe the checking conditions in more detail when necessary |  |
| What is the behavior when one subscribed GOOSE message isn’t received or syntactically incorrect (missing GOOSE) |  |
| What is the behavior when one subscribed GOOSE message exceeds the previous time Allowed to Live (TAL) |  |
| What is the behavior when a subscribed GOOSE message is out-of-order |  |
| What is the behavior when a subscribed GOOSE message is duplicated |  |
| May the GOOSE data set contain structured data objects? | Y/N |
| <additional items> |  |

PIXIT for Control model

| Description | Value / Clarification |
| --- | --- |
| What control modes are supported | Y/N status-only Y/N direct-with-normal-security Y/N sbo-with-normal-security Y/N direct-with-enhanced-security Y/N sbo-with-enhanced-security |
| Is Time activated operate (operTm) supported | Y/N |
| Is “operate-many” supported | Y/N |
| Can the client set the test flag? | Y/N |
| What check conditions can be set | Y/N synchrocheck Y/N interlock-check |
| Which originator categories are supported and what is the originator identification? |  |
| Describe if and how the client sets/increments the ctlNum |  |
| What does the client do when it receives a LastApplicationError and describes how to view the additional cause? | For example display / store the AddCause |
| What does the client do when it receives a Select, SelectWithValue or Operate respond negative ? | For example display error |
| Can the client change the control model via online services? |  |
| What does the client do when the ctlModel is not initialized in the SCL? |  |
| Describe how the client responds when it receives a positive Command Termination |  |
| Describe how the client responds when it receives a negative Command Termination |  |
| Describe how the client responds when it receives a negative Operate response |  |
| <additional items> |  |

PIXIT for Time and time synchronisation model

| Description | Value / Clarification |
| --- | --- |
| Described how to view the internal time & quality or how to expose the timestamp and timestamp quality via the IEC 61850 interface | View: Expose: for example in Operate request |
| What time quality bits are supported | Y/N LeapSecondsKnown Y/N ClockFailure Y/N ClockNotSynchronized |
| What is the behavior when the time synchronization signal/messages are lost |  |
| When is the quality bit "ClockFailure" set? |  |
| When is the quality bit "ClockNotSynchronised” set? |  |
| <additional items> |  |

PIXIT for File transfer model

| Description | Value / Clarification |
| --- | --- |
| Describe when or how to force the client to request GetServerDirectory(FILE) and what it does with the responded filenames |  |
| Does the client uses a wildcard in the GetServerDirectory(FILE) request | Yes, wildcard = “*” or “*.*” No |
| Does the client support IEDs that include the path in the file name in the GetServerDirectory(FILE) respond? | Y/N path included Y/N path not included |
| Does the client support IEDs that use the file separator | Y/N “/” Y/N “\” |
| What is the maximum file name size including path |  |
| Can the client read a file with size 0 | Y/N |
| Are directory/file name case sensitive | Case sensitive / Not case sensitive |
| Maximum file size |  |
| Describe how the client behaves in case of: GetFileAttributes response- |  |
| <additional items> |  |

# Footnotes

GetXxxDirectory = GetServerDirectory, GetLogicalDeviceDirectory, GetLogicalNodeDirectory(DATA), GetDataDirectory and GetDataDefinition

# Text boxes

Utrechtseweg 310, 6812 AR Arnhem, the Netherlands.

Telephone +31 26 3 56 91 11. Telefax + 31 26 3 51 56 06.

Copyright © KEMA Nederland B.V., Arnhem, the Netherlands. All rights reserved.

This document  may be distributed to UCA international users group members only.

KEMA Nederland B.V. and/or its associated companies disclaim liability for any direct, indirect, consequential or incidental damages that may result from the use of the information or data, or from the inability to use the information or data.

Ethernet Hub or Managed switch with mirror port

Client Device Under Test (DUT)

ANALYZER

SERVER SIMULATOR 1

TIME SERVER

SERVER SIMULATOR N

HMI (integrated in DUT or

protocol simulator)