Test Procedures Change List (TPCL) for

IEC 61850 server test procedures revision 2.4

Version 1.6

UCA International Users Group

Testing Sub Committee

Date: July 28, 2012

Introduction

Problems that are uncovered during conformance testing that impact the IEC 61850 Standard are taken back through the TISSUES Process. However, there are some problems that relate only to the content of the Test Procedures. The UCAiug is the owner of the Test Procedures and so has the responsibility for tracking changes. Given the long time lag between major versions, we have a need to track interim changes that may impact testing. This “Test Procedures Change List (TPCL)" document specifies such interim changes. The UCAiug test sub committee reviews and approves each change.  Changes resulting in new test procedures shall be specified in the next revision of the test procedures.

This list:

- Contains changes to the most recent (server) test procedures

- Indicate if a change is:

- Accepted, resulting in a clarified test procedure (included after the change list table)

- Denied

- Added to the next revision

- Shall be used by recognized/accredited test labs

- Should be referenced in the test report only

- Is available at the UCAiug sharepoint for test sub committee members

Table of Contents

TPCL Revision History	4

TPCL 1.6	6

References	6

Proposed Approved Change List	6

Clarified Test Procedures	7

PIXIT template changes	14

Certificate template changes	15

TPCL 1.5	18

References	18

Approved Change List	18

List of denied and next revision changes	20

Clarified Test Procedures	20

PIXIT template changes	28

Certificate template changes	29

# TPCL Revision History

| Revision | Changes |
| --- | --- |
| 1.0 | Initial version |
| 1.1 | Updated expected behavior in CtlN2 to allow reset of select timeout again. However the recommended behavior is a negative respond on the second select (and this behaviour will be mandatory in the next version of the server test procedures). Update test FtN1 to test for both empty and invalid file names in a GetFileAttributeValues. Updated Srv6, removed EX at step 2 because its already used in step 1 |
| 1.2 | Updated server test specification to version 2.3 and removed all TPCL elements Removed text “This list: …should be referenced in the test report only” (the TPCL is now referenced on the conformance certificate). |
| 1.3 | Add verification of Ed2 LN in Ed1 devices = Mdl12 |
| 1.4 | note in the TPCL denied list that the number of test cases on the certificate template is correct |
| 1.5 | Srv6 updated to use the SCL valKind and remove PIXIT reference Update certificate template to reduce the references to TPCL (explain the abbreviations?) and to harmonize the format with the client certiifcate Update PIXIT template entries: Rp7 (bytes or nr.of.reports), Go9 specify datatypes instead of CDC and Go10/Go11, Go13 Ft1: zip or COMTRADE supported Zip structure: all files in the same folder, in subfolders, etc. Add 2 entries: COMTRADE files zipped Y/N when yes the structure of the files in the zip. (I assume these are just the one xxxx.cfg and on xxxx.dat file, I don't see a need for structure in the zip) Update Rp2/Br2 to move the sequence number increment expected result to Rp3/Br3 Update Rp4 to verify non-null RptID in the RCB and Report Sequence of data attribute in a data object is only applicable for the same functional constraints Update the Sg2 testcase to verify "several" settings not all. Ctl3 – select all SBO objects or just multiple – the abstract and detailed testprocedure are not consistent DSetN6/DSetN7 the maximum number of datasets may be exceeded – updated the expected result When Sg3 is conditional SgN1a part 2 is also conditional. However part 1 and 3 are mandatory – no change TISSUE Template for test procedure 2.3: tissue #60 (part 7-3) is only applicable for ed.2 therefore should be removed from TICS for test procedure 2.3 Propose to add new Gos test case to verify the behavior when the quality in one of the dataset elements is set to "test" or invalid.( Denied this is application logic not firmware) RpN5 include the Resv to the list of attributes at step 2 |
| 1.6 | Updated GOOSE Test Cases and PIXIT |

# TPCL 1.6

## References

Conformance Test Procedures for Server Devices with IEC 61850-8-1 interface,

Revision 2.4, July 28, 2012

## Proposed Approved Change List

| ID | TEST CASE | CHANGE | FINAL PROPOSAL | RESULT |
| --- | --- | --- | --- | --- |
| 1 | Gop1 | Added comment to document the conditional. | See new test procedure Gop1 |  |
| 2 | Gop6 | Added comment to document the conditional. | See new test procedure Gop6 |  |
| 3 | Gop7a | Revised test procedure for clarification. Changed test case from mandatory to conditional. | See new test procedure Gop7 |  |
| 4 | Gop7a | Added test procedure so that GOOSE only DUTs can be tested. Test case is mandatory for those DUT declaring support for GOOSE. | See new test procedure Gop7a |  |
| 5 | Gop8 | Revised test procedure for clarification. | See new test procedure Gop8 |  |
| 6 | Gop9 | Revised test procedure for clarifications. Changed test case from mandatory to conditional. | See new test procedure Gop9 |  |
| 7 | Gop9a | Added test procedure so that GOOSE only DUTs can be tested. Test case is mandatory for those DUT declaring support for GOOSE. | See new test procedure Gop9a |  |
| 8 | Gop9b | Added test procedure to check that clients are not allowed to write a DatSet reference to a value of NULL. | See new test procedure Gop9b |  |
| 9 | Gop10 | Added conditionals as comment. | See new test procedure Gop9b |  |
| 10 | GopN1 | Corrected test procedure to correctly test read-only. | See new test procedure GopN1 |  |
| 11 | GopN2 | Revised test procedure for clarifications. Changed test case from mandatory to conditional. | See new test procedure GopN2 |  |
| 12 | GopN2a | Added test procedure so that GOOSE only DUTs can be tested. Test case is mandatory for those DUT declaring support for GOOSE. | See new test procedure GopN2a |  |
| 13 | GosN5 | Changed name and test procedure for clarity. | See new test procedure GopN5 |  |
| 14 | GosN6 | Changed name and test procedure for clarity. | See new test procedure GopN6 |  |

## Clarified Test Procedures

#### Clarified Modelling Test Procedures (in alphabetical order)

| Gop1 | GetLogicalNodeDirectory(GoCB) and GetGoCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.2.5 IEC 61850-8-1 clause 18.1.2.3 |
| Expected result 1. DUT sends GetLogicalNodeDirectory(GoCB) response+ with a list of GoCB’s. The object reference shall be “LDName/LLN0.GoCBName” 2. DUT sends GetGoCBValues response+ |
| 9Test description 1. For each logical node Client requests GetLogicalNodeDirectory(GoCB) 2. For each GoCB Client requests GetGoCBValues() |
| Comment: Conditional upon declaration of support for GetGoCBValues, GetLogicalNodeDirectory, and ServerSide Two-party association. |

| Gop6 | SetGoCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.3, 15.2.2.5, 15.2.2.6 IEC 61850-8-1 clause |
| Expected result DUT sends a SetGoCBValues response+ and stops transmitting GOOSE messages DUT sends a SetGoCBValues response+ and initializes/starts transmitting GOOSE messages. The first message has stNum=1. |
| Test description Client requests a SetGoCBValues with GoEna set to FALSE Client requests a SetGoCBValues with GoEna set to TRUE |
| Comment GoEna is the only attribute that may be written according to part 8-1. Conditional upon declaration of support for ServerSide TwoParty Association and SetGoCBValues. |

| Gop6 | SetGoCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.3, 15.2.2.5, 15.2.2.6 IEC 61850-8-1 clause |
| Expected result DUT sends a SetGoCBValues response+ and stops transmitting GOOSE messages DUT sends a SetGoCBValues response+ and initializes/starts transmitting GOOSE messages. The first message has stNum=1. |
| Test description Client requests a SetGoCBValues with GoEna set to FALSE Client requests a SetGoCBValues with GoEna set to TRUE |
| Comment GoEna is the only attribute that may be written according to part 8-1. Conditional upon declaration of support for ServerSide TwoParty Association and SetGoCBValues. |

| Gop7a | Configuration revision matches SCL file contents | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.6, clause 15.2.3.9 IEC 61850-8-1 clause 18.1.1, 18.1.2.1, 18.1.2.4, 18.1.2.5, Annex A |
| Expected result 3). DUT restarts 4). DUT sends GOOSE message with ConfRev matching SCL file. |
| Test description SCL file for DUT is updated with new confRev value. Test engineer causes the DUT to be reconfigured with the SCL file. Test engineer restarts the DUT. DUT transmits GOOSE message. |
| Comment: |

| Gop7b | Configuration revision matches SCL file contents | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.6, clause 15.2.3.9 IEC 61850-8-1 clause 18.1.1, 18.1.2.1, 18.1.2.4, 18.1.2.5, Annex A |
| Expected result 2). DUT restarts 3). DUT sends a GetGoCBValues response+ with the same ConfRev (not null) value as configured in the SCL file. 4). DUT sends GOOSE message with the same ConfRev value as declared in the SCL file. |
| Test description Test engineer obtains SCL file containing DUT ConfRev. Test engineer restarts the DUT Client request GetGoCBValues(). Enable GoCB when necessary and wait for GOOSE message through SetGoCBValues() if PICS shows support. Otherwise, the DUT is expected to transmit the GOOSE. |
| Comment: This test is for those DUTs declaring support for GetGoCBValues and ServerSide TwoParty Association. PICS must show support for GetGoCBValues as well as SendGOOSE. |

| Gop8 | Configuration revision updates when associated DatSet is changed online | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.6 IEC 61850-8-1 clause |
| Expected result DUT sends a GetGoCBValues response+ with incremented ConfRev value DUT sends GOOSE message with incremented ConfRev value |
| Test description Test engineer deletes the first member of the GoCB data set in the SCL file. Test engineer causes the DUT to be reconfigured with the SCL file. Client requests a GetGoCBValues() Client waits for GOOSE message Test engineer re-orders the first and last member of the GoCB data set through the SCL file; repeat step 2-4 Test engineer changes the value of the GoCB data set through the SCL file; repeat step 2-4 |
| Comment: Conditional on declaration of support for: GetGoCBValues, SetGoCBValues, and ServerSide TwoParty Association. |

| Gop9a | Ensure that NULL data sets are not sent. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1 Tissue #333, PIXIT |
| Expected result 3. DUT Restarts 5. DUT shall not send a GOOSE for the GOCB message or sets NdsComm per PIXIT. |
| Test description Test engineer changes an SCL file to have a NULL data set reference in a GoCB. Test engineer causes the DUT to be reconfigured with the SCL file. Test engineer restarts DUT. Test engineer, if needed, uses some means to attempt to enable the GOCB. Wait 1 minute. |

| Gop9b | Ensure that NULL data sets are either refused or result in NdsCom=TRUE. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1 Tissue #333, PIXIT |
| Expected result 3. DUT restarts 4. DUT sends SetGoCBValues response+ or – depending upon PIXIT declaration. 5. DUT sends a GetGoCBValues response+ with NdsCom=TRUE conditional upon support for GetGoCBValues being declared and GoCB.enable = TRUE. 6. DUT does not send GOOSE message for GOCB that has a NULL DatSet value message or sets NdsComm per PIXIT. |
| Test description 1. Test engineer changes an SCL file to have a NULL data set reference in a GoCB. 2. Test engineer causes the DUT to be reconfigured with the SCL file. 3. Test engineer restarts DUT. 4. Test engineer enables GoCB using SetGoCBValues. 5. Client requests a GetGoCBValues() 6. Wait one minute. |
| Comment: This test is for DUTs that declare support for GetGoCBValues ,SetGoCBValues, and ServerSide TwoParty Association. |

| Gop10 | GOOSE with data attributes (FCDA) and data objects (FCD) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2 IEC 61850-8-1 clause 18.1 PIXIT |
| Expected result 1. DUT sends a GOOSE messages with data attributes 2. DUT sends a GOOSE messages with data objects |
| Test description Verify the DUT is able to send GOOSE message with data attributes (FCDA) Verify the DUT able to send GOOSE message with data objects (FCD) |
| Comment: Conditional upon declaration of support of FCDs as data set members. |

| GopN2a | Ensure behaviour of GOOSE when data set contents are too large. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1 PIXIT |
| Expected result 1. DUT Restarts 3. DUT does not send GOOSE message or sets NdsComm per PIXIT. |
| Test description Test engineer activates the DUT that has a GoCB configured with a data set that is too large for GOOSE (configuration through an SCL file). Test engineer enables, through local means, the GoCB if needed. Test engineer waits 1 minute. |
| Comments: Conditional upon support for PIXIT ability to have user defined DatSet values. |

| GopN2b | Ensure behaviour of GOOSE when data set contents are too large. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result 1. DUT Restarts 2. DUT responds with one of the following, per PIXIT: SetGoCBValues response- or SetGoCBValues response+ 3. GetCoCBValues returns: For (2) Response+: GoEna=TRUE and NdsCom= TRUE; For (2) Response-: GoEna=FALSE and NdsCom= TRUE. 4. DUT does not send the GOOSE message or sets NdsComm per PIXIT. |
| Test description Test engineer activates the DUT that has a GOCB configured with a data set that is too large for GOOSE. Test engineer uses SetGoCBValues to enable the GOCB. Test engineer uses GetGoCBValues to determine state of GoCB. Test engineer waits 1 minute. |
| Conditional upon support for SetGoCBvalues , GetGoCBValues, ServerSide Two Party Association, and PIXIT ability to use non-predefined DataSets. |

| GosN5 | No GOOSE message received with publication continuing | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result DUT indicates that subscribed GOOSE message isn’t received (PIXIT) DUT indicates that subscribed GOOSE message is received again (PIXIT) DUT indicates that subscribed GOOSE message isn’t received (PIXIT) DUT behaves as specified in the PIXIT |
| Test description Test engineer configures the DUT as specified Publisher sends correct GOOSE message with no value changes (same stNum) Publisher is disconnected from the network, continues to send GOOSE messages for 30 seconds with no state change (e.g. same stNum as step 2). Publisher is reconnected to the network and continues to send GOOSE messages (same stNum) Publisher is disconnected from the network, continues to send GOOSE messages for 30 seconds with no state change (e.g. same stNum as step 2). Publisher is reconnected to the network and continues sends GOOSE messages indicating a state change (incremented stNum, sqNum other than 0) |
| Comment |

| GosN6 | GOOSE message does not match DUT SCL configuration | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1, 15.2.3 IEC 61850-8-1 clause 18.1, Annex C, PIXIT |
| Expected result DUT responds as specified in the PIXIT |
| Test description Test engineer configures the DUT as specified below and Publisher sends several GOOSE messages with data value change with correct status and sequence numbers with an initial or stNum change: GoCB reference = mismatch with expected GoCB from SCL , NULL timeAllowedtoLive = 0 datSet reference = mismatch with GoCB from SCL, NULL goID reference = mismatch with GoCB from SCL, NULL timestamp of status change = plus one hour, minus one hour, 0 confRev = mismatching with GoCB from SCL numDatSetEntries does not match the expected number of DataSet element members as configured by SCL. The confRev remains as expected, but the numDatSetEntries changes +1 or -1 and the allData matches the number of numDatSetEntries. values of allData entries(same DatSetReference, same expected ConfRev) = out-of-order APPID = different from SCL and 0 |
| Comment |

## PIXIT template changes

| Go3 | What is the behaviour when the GOOSE publish configuration is incorrect | DUT will set NdsCom=TRUE and GoEna = FALSE or DUT keeps GoEna=TRUE and NdsCom=TRUE DUT will send GOOSE message (Yes/No): |
| --- | --- | --- |
| Go15 | What is the initial GOOSE message sqNum upon DUT restart (Gop3) |  |
| Go16 | For a NULL or Too Large DatSet, what is the response to a SetGoCBValue for GoEna=TRUE (Gop9) | Response- Response+ |

## Certificate template changes

| IEC 61850 Certificate Level A/B1 | No. << certificate number>> |
| --- | --- |
| Issued to: | For the product: |
| <<TEST INITIATOR>> <<FULL ADDRESS>> | <<PRODUCT NAME>> <<VERSION NUMBER>> <<ADDITIONAL INFO>> |

Issued by: <<test tlab>>

The product has not shown to be non-conforming to:

IEC 61850-6, 7-1, 7-2, 7-3, 7-4 and 8-1

Communication networks and systems in substations

The conformance test has been performed according to IEC 61850-10, the UCA International Users Group Device Test Procedures version 2.3 with TPCL2 version 1.x, the product’s protocol, model and technical issue implementation conformance statements: “<<PICS>>”, “<<MICS>>”, “<<TICS>>” and the extra information for testing: “<<PIXIT>>”.

The following IEC 61850 conformance blocks have been tested with a positive result (number of relevant and executed test cases / total number of test cases):

| 1 Basic Exchange (../24) 2 Data Sets (../6) 2+ Data Set Definition (../23) 3 Substitution (../4) 4 Setting Group Selection (../3) 4+ Setting Group Definition (7/7) 5 Unbuffered Reporting (../19) 6 Buffered Reporting (../21) | 9a GOOSE Publish (../13) 9b GOOSE Subscribe (../11) 12a Direct Control (../12) 12b SBO Control (../14) 12c Enhanced Direct Control (../13) 12d Enhanced SBO Control (../19) 13 Time Synchronization (../5) 14 File Transfer (../7) |
| --- | --- |

This Certificate includes a summary of the test results as carried out at <<CITY>> in <<COUNTRY>> with <<CLIENT SIMULATOR> <<VERSION>> with test suite <<VERSION>> and <<ANALYZER>> <<VERSION>>. The test is based on the UCA International Users Group Device Test Procedures version 2.3. This document has been issued for information purposes only, and the original paper copy of the <<TESTLAB>> report: No. <<TESTREPORT NUMBER>> will prevail.

The test has been carried out on one single specimen of the product as referred above and submitted to <<TESTLAB>> by <<TEST INITIATOR>>. The  manufacturer’s production process has not been assessed. This certificate does not imply that <<TESTLAB>> has certified or approved any product other than the specimen tested.

<<CITY>>, <<DATE>>

<<Manager NAME>>	<<Tester NAME>>

<<JOB TITLE>>	<<JOB TITLE>>

1 Level A - Independent Test lab with certified ISO 9000 or ISO 17025 Quality System

1 Level B - Tester with ISO 9000 or ISO 17025 Quality System

2 TPCL - Test procedures change list

Applicable Test Procedures from the UCA International Users Group Device Test Procedures version 2.3 with TPCL version 1.x

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | Ass1, Ass2, Ass3, AssN2, AssN3, AssN4, AssN5 Srv1, Srv2, Srv3, Srv4, Srv5, SrvN1abcd, SrvN4 | AssN6 Srv6, Srv7, Srv8, Srv9, Srv10, SrvN1e, SrvN1f, SrvN2, SrvN3 |
| 2: Data Sets | Dset1, Dset10a, DsetN1ae | Dset10b, DsetN1b, DsetN16 |
| 2+: Data Set Definition | Dset2, Dset3, Dset4, Dset5, Dset6, Dset7, Dset8, Dset9 DsetN1cd, DsetN2, DsetN3, DsetN4, DsetN5, DsetN6, DsetN7, DsetN8, DsetN9, DsetN10, DsetN11, DsetN12, DsetN13, DsetN14, DsetN15 |  |
| 3: Substitution | Sub1, Sub2, Sub3, SubN1 |  |
| 4: Setting Group Selection | Sg1, SgN1a | Sg3 |
| 4+: Setting Group Definition | Sg2, Sg4, SgN1b, SgN2, SgN3, SgN4, SgN5 |  |
| 5: Unbuffered Reporting | Rp1, Rp2, Rp3, Rp4, Rp7, Rp10, Rp12 RpN1, RpN2, RpN3, RpN4 | Rp5, Rp6, Rp8, Rp9, Rp11, RpN5, RpN6, RpN7 |
| 6: Buffered Reporting | Br1, Br2, Br3, Br4, Br7, Br8, Br9, Br12, Br14 BrN1, BrN2, BrN3, BrN4, BrN5 | Br5, Br6, Br10, Br11, Br13, BrN6, BrN7 |
| 6+: Enhanced buffered reporting | BrE1, BrE2, BrE3, BrE6, BrE7, BrE8, BrE9, BrE10, BrE11 | BrE4, BrE5, BrE12 |
| 9a: GOOSE publish | Gop2, Gop3, Gop4, Gop7a, Gop9a,Gop10a | Gop1, Gop5, Gop6, Gop7, Gop8, Gop9, Gop9b,Gop10b, GopN1, GopN2,Gopn2a |
| 9b: GOOSE subscribe | Gos1a, Gos2, Gos3, GosN1, GosN2, GosN3, GosN4, GosN5, GosN6 | Gos1b, Gos4 |
| 12a: Direct control | CtlN3, CtlN8 DOns1, DOns3 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 DOns2, DOns4, DOns5 |
| 12b: SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, SBOns2 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 SBOns3, SBOns4, SBOns5 |
| 12c: Enhanced Direct Control | CtlN3, CtlN8 DOes2, DOes5 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11 DOes1, DOes3, DOes4 |
| 12d: Enhanced SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, CtlN9 SBOes1, SBOes2, SBOes3 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11 SBOes4, SBOes5, SBOes6, SBOes7 |
| 13: Time sync | Tm1, Tm2, TmN1 | Tm3, TmN2 |
| 14: File transfer | Ft1, Ft2ab, Ft4, FtN1ab | Ft2c, Ft3, FtN1c |

[ All configuration file and data model tests have been successfully performed for the product variants using the same hardware and software version: <<Variant2>>, <<Variant3>> ]

# TPCL 1.5

## References

Conformance Test Procedures for Server Devices with IEC 61850-8-1 interface,

Revision 2.3, August 17, 2011

## Approved Change List

| ID | TEST CASE | CHANGE | FINAL PROPOSAL | RESULT |
| --- | --- | --- | --- | --- |
| 1 | Mdl12 | Define the use of name spaces for Ed2 LN used in Ed1 devices | See new test procedure Mdl12 |  |
| 2 | Srv6 | The read/write ability may be indicated in the SCL using the valKind="Set" or "RO" | See new test procedure Srv6 |  |
| 3 | Certificate | Include a reference to the TPCL and reduce the text where possible | See new template |  |
| 4 | PIXIT | Update PIXIT template for: Rp7 (bytes or nr.of.reports), Go9 specify datatypes instead of CDC and Go10/Go11, Go13 Ft1: zip or COMTRADE supported Zip structure: all files in the same folder, in subfolders, etc. Add 2 entries: COMTRADE files zipped Y/N when yes the structure of the files in the zip. (I assume these are just the one xxxx.cfg and on xxxx.dat file, I don't see a need for structure in the zip) | Attached |  |
| 5 | Rp2/Rp3 Br2/Br3 | Move the expected result "sequence number increment" from Rp2 to Rp3 | Attached |  |
| 6 | RptID | An intoperability was reported caused by indexing an RptID. | Extend Rp4 to verify a non-null RptID, Attached |  |
| 7 | Data model | Figure 3 in IEC 61850-8-1 states that the order of Functional Constraints is just a recommendation! | Verify only the order of data attributes with the FC |  |
| 8 | Sg2 | Changing all settings to a new value is very complicated and may result in issue for testing | Reduce "all" by several or one for each datatype of setting, Attached |  |
| 9 | Ctl3 | Select all control object or just multiple. The abstract test case and detailed test procedures are not consistent | Make consistent to multiple, attached |  |
| 10 | DsetN6 DsetN7 | The maximum number of datasets may be exceeded. Update the expected result | Update the expected result, attached |  |
| 11 | TICS | TISSUE #60 is Ed2 and shall be removed from the template | Remove #60 |  |
| 12 | RpN5 | Resv attribute is missing in the list of step 2 | Add Resv, Attached |  |

## List of denied and next revision changes

| ID | TEST CASE | CHANGE | FINAL PROPOSAL | RESULT |
| --- | --- | --- | --- | --- |
| 1 | - | The certificate template specifies the number of test per conformance blocks. We assumed the total number was incorrect | After second analysis the total numbers of test cases specified in the table on the front page of the certificate is correct | No change |
| 2 | Sg3, SgN1a | Sg3 is conditional as such SgN1a should be conditional as well | NO only part 2 of SgN1a is conditional part 1 and 3 are mandatory | No change |
| 3 | Gos | What is the expected result when a subscribed goose element has quality "test"? Its probably ignored just like "invalid" | This is related to application logic and less to firmware. | No change |

## Clarified Test Procedures

#### Clarified Modelling Test Procedures (in alphabetical order)

| Mdl10 | Check if the order of the data attributes with the same functional constraint of the Data Object type match with IEC 61850-7-3 Passed when all data attributes are in matching order | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |

| Mdl12 | Ed2 data model extensions in Ed1 device | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-1 clause 14 IEC 61850-7-4 Ed2 |
| Expected result The SCL file of the Ed1 device Shall use 7-3 Ed1 CDC's also for the Ed2 LN Data objects Shall use INS/INC/ING instead of ENS/ENC/ENG Shall NOT use 7-3 Ed2 specific CDC's as for example: VSS, VSG, TSG as ORG Shall only use the part 8-1 Ed1 basic data types (for example no INT64) The use of name space is as follows: ldNs = IEC 61850-7-4:2003 Ed1 LN don't need a lnNs Ed2 LN shall have lnNs = IEC 61850-7-4:2007 Presence and order of Data Objects (DO) Ed1 LN shall have the mandatory DO's according to Ed1 Ed2 LN shall have the mandatory DO's according to Ed2 Ed1 LN shall have the DO's in the same order as specified in Ed1 The order of DO's for Ed2 LN is not required anymore and not verified The use of dataNs is as follows A private DO in any Ed1/Ed2 LN shall have a private dataNs value A private DO in a private LN does not need a dataNs An Ed1 DO in a Ed1 LN does not need a dataNs An Ed2 DO in a Ed2 LN does not need a dataNs An Ed2 DO in an Ed1 LN shall have dataNs = IEC 61850-7-4:2007 Note: the presence of the name space attribute is not a valid criterion anymore. When a name space is not needed it means: either the name space is not present or the name space has the same value as the name space on the higher level |
| Test description Scan SCL file for Ed2 logical nodes types and dataobjects |
| Comment Ed2 LN types that have a mandatory DO with an Ed2 specific CDC are not allowed |

Clarified Communication Test Procedures (in alphabetical order)

| Ctl3 | Select multiple SBO control objects and cancel them in opposite order |
| --- | --- |

| Ctl3 | Select/Cancel multiple SBO control objects | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result DUT sends SelectWithValue response+ for non-interlocked objects and response- with AddCause "1-of-n control" for interlocked objects (PIXIT) DUT sends Select response+ for non-interlocked objects and response- for interlocked objects (PIXIT) DUT sends Cancel response+ for selected objects |
| Test description Client request SelectWithValue for multiple SBOes control objects Client requests Select for multiple SBOns control objects Client request Cancel for the selected control objects in reverse order |
| Comment |

| DsetN6 | Create persistent data set with more than max. no of data members | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT? |
| Expected result 1. The DUT responds with a CreateDataSet response- or response+ when resources are still available |
| Test description 1. Client requests a persistent CreateDataSet with the maximum number + 1 of data members as supported by the DUT |
| Comment |

| DsetN7 | Create non-persistent data set with more than max. no of data members | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT? |
| Expected result 1. The DUT responds with a CreateDataSet response- or response+ when resources are still available |
| Test description 1. Client requests a non-persistent CreateDataSet with the maximum number + 1 of data members as supported by the DUT |
| Comment |

Note: The max is defined in the SCL services section. So no PIXIT entry is required.

| Rp2 | Reporting of optional fields for a URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.8 IEC 61850-8-1 clause 17.1.1.1, 17.2.1, PIXIT |
| Expected result 1. DUT sends SetURCBValues response+ for supported optional fields and response- when one of the optional fields isn’t supported 2. DUT sends SetURCBValues response+ 3. DUT sends a correct report according to trigger condition and IEC 61850-8-1 table 40 with all data set members for reason integrity and otherwise only the changed members. The configured and reported optional fields should match the sequence number is incremented and starts with 0 the report time stamp is in UTC format and matches the trigger time the reason for inclusion matches the trigger condition the configured and reported data set name do match the data-reference(s) match the data set member(s) Configuration revision matches the URCB configuration When segmentation is set the report includes sub sequence number and more segments follow 4. DUT sends SetURCBValues response+ and sends no reports anymore |

| Rp3 | Trigger conditions for a URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.11 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1, PIXIT |
| Expected result 1. DUT sends SetURCBValues response+ for supported trigger conditions and response- when one of the trigger conditions isn’t supported 2. DUT sends SetURCBValues response+ 3. DUT sends a report according to trigger condition integrity reports should be transmitted immediately at timeout data change reports are transmitted immediately when BufTm=0 data change reports are transmitted after BufTm of first data change when BufTm>0 the sequence number is incremented 4. The configured and reported optional fields should match 6. DUT does not sends reports |

| Rp4 | General interrogation URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.13 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1 |
| Expected result 3. DUT sends SetURCBValues() response+ and then sends GI report with the configured RptID 4. DUT sends GetURCBValues() response+ with GI attribute not set |
| Test description 1. Client configures an available URCB with a valid non-null RptID value 2. Client enables the URCB 3. Client requests SetURCBValues() to set the GI report 4. Client requests GetURCBValues() 5. Client disables the URCB |
| Comment |

| RpN5 | Exclusive use of URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1 IEC 61850-8-1 clause 17.1.1.2, Tissue #114 |
| Expected result 2. DUT sends SetURCBValues() response- 4. DUT sends SetURCBValues() response+ 8. DUT sends SetURCBValues() response+ |
| Test description 1. Client1 reserves an available URCB 2. Client2 configures the same URCB by requesting SetURCBValues() with one of the following attributes Resv, RptID, DatSet, OptFlds, BufTm, TrgOps, IntgPd 3. Client1 resets the reservation of the URCB 4. Client2 reserves and configures the URCB 5. Client2 resets the reservation of the URCB 6. Client1 reserves the URCB 7. Client1 aborts and re-establishes the association 8. Client1 configures the URCB 9. Client1 resets the reservation of the URCB |
| Comment |

| Sg2 | SelectEditSG, SetSGValues, ConfirmEditSGValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2 |
| Expected result 1. DUT sends SelectEditSG response+ 2. DUT sends SetSGValues [FC=SE] response+ 3. DUT sends GetSGValues [FC=SE] response+ 4. DUT sends ConfirmEditSGValues response+, the value of CnfEdit shall return to FALSE once the storage is completed. |
| Test description Client requests SelectEditSG Client requests SetSGValues [FC=SE] with at least one valid value for each data type in the group Client requests GetSGValues [FC=SE] to verify the new values Client requests ConfirmEditSGValues |
| Comment Note: Sg3 must be executed after Sg2 to verify changed values are active |

| Srv6 | SetDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.2 PIXIT |
| Expected result 1. DUT sends SetDataValues(FC= ST, MX, EX) response- 2. DUT sends SetDataValues(FC= CF,SP,SE,DC) response- for read-only data and response+ for write enabled data as specified in the ICD using valKind="RO" for read-only and "Set" for write eabled data attributes. In case the valKind is missing in the ICD the data attribute may be writable or read-only. 3. and 5. DUT sends SetDataValues response+ 4. and 6. DUT sends GetDataValues response+ with requested value, the value does match |
| Test description 1. For each data object client sends a SetDataValues(FC=ST, MX,EX) with the current value 2. For each data object client sends a SetDataValues(FC=CF,SP,SE,DC) with the current value For the first write-enabled data object (if any) 3. Client sends a SetDataValues with a valid new value 4. Client sends a GetDataValues request and check the value does match 5. Client sends a SetDataValues with the original value 6. Client sends a GetDataValues request and check the value does match |
| Comment |

Note: This test passes when the IED behaves as specified by the valKind in the SCL.  If no valKind is present the data attribute may be writable.

In Ed2 of the server test procedures the valKind shall be mandatory in case a FC=CF/SP/SE/DC is read-only because the default value of valKind = "Set".

## PIXIT template changes

| Rp7 | What is the buffer size for each BRCB or how many reports can approximately be buffered | <number of bytes or typical number of dataset members or reports> |
| --- | --- | --- |

| Go10 | Published FCD supported common data classes / data types are | <list of common data classes / data types> |
| --- | --- | --- |
| Go11 | Subscribed FCD supported common data classes / data types are | <list of common data classes / data types> |

Should all data types be supported as publisher? Discuss at the next WG10 meeting.

| Go13 | What is the minimum supported retransmission time? What is the maximum supported retransmission time? Is it fixed or configurable? | <minTime> <maxTime> Fixed / Configurable |
| --- | --- | --- |

| Ft1 | What is structure of files and directories? Where are the COMTRADE files stored? Are comtrade files zipped and what files are included in each zip file? | <Flat file system with pseudo folders or file system with folders> /COMTRADE/ or /LD/<IED+LD>/COMTRADE Not zipped and/or Zipped <Zip includes: .cfg and .dat> |
| --- | --- | --- |

## Certificate template changes

| IEC 61850 Certificate Level A/B1 | No. << certificate number>> |
| --- | --- |
| Issued to: | For the product: |
| <<TEST INITIATOR>> <<FULL ADDRESS>> | <<PRODUCT NAME>> <<VERSION NUMBER>> <<ADDITIONAL INFO>> |

Issued by: <<test tlab>>

The product has not shown to be non-conforming to:

IEC 61850-6, 7-1, 7-2, 7-3, 7-4 and 8-1

Communication networks and systems in substations

The conformance test has been performed according to IEC 61850-10, the UCA International Users Group Device Test Procedures version 2.3 with TPCL2 version 1.x, the product’s protocol, model and technical issue implementation conformance statements: “<<PICS>>”, “<<MICS>>”, “<<TICS>>” and the extra information for testing: “<<PIXIT>>”.

The following IEC 61850 conformance blocks have been tested with a positive result (number of relevant and executed test cases / total number of test cases):

| 1 Basic Exchange (../24) 2 Data Sets (../6) 2+ Data Set Definition (../23) 3 Substitution (../4) 4 Setting Group Selection (../3) 4+ Setting Group Definition (7/7) 5 Unbuffered Reporting (../19) 6 Buffered Reporting (../21) | 9a GOOSE Publish (../13) 9b GOOSE Subscribe (../11) 12a Direct Control (../12) 12b SBO Control (../14) 12c Enhanced Direct Control (../13) 12d Enhanced SBO Control (../19) 13 Time Synchronization (../5) 14 File Transfer (../7) |
| --- | --- |

This Certificate includes a summary of the test results as carried out at <<CITY>> in <<COUNTRY>> with <<CLIENT SIMULATOR> <<VERSION>> with test suite <<VERSION>> and <<ANALYZER>> <<VERSION>>. The test is based on the UCA International Users Group Device Test Procedures version 2.3. This document has been issued for information purposes only, and the original paper copy of the <<TESTLAB>> report: No. <<TESTREPORT NUMBER>> will prevail.

The test has been carried out on one single specimen of the product as referred above and submitted to <<TESTLAB>> by <<TEST INITIATOR>>. The  manufacturer’s production process has not been assessed. This certificate does not imply that <<TESTLAB>> has certified or approved any product other than the specimen tested.

<<CITY>>, <<DATE>>

<<Manager NAME>>	<<Tester NAME>>

<<JOB TITLE>>	<<JOB TITLE>>

1 Level A - Independent Test lab with certified ISO 9000 or ISO 17025 Quality System

1 Level B - Tester with ISO 9000 or ISO 17025 Quality System

2 TPCL - Test procedures change list

Applicable Test Procedures from the UCA International Users Group Device Test Procedures version 2.3 with TPCL version 1.x

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | Ass1, Ass2, Ass3, AssN2, AssN3, AssN4, AssN5 Srv1, Srv2, Srv3, Srv4, Srv5, SrvN1abcd, SrvN4 | AssN6 Srv6, Srv7, Srv8, Srv9, Srv10, SrvN1e, SrvN1f, SrvN2, SrvN3 |
| 2: Data Sets | Dset1, Dset10a, DsetN1ae | Dset10b, DsetN1b, DsetN16 |
| 2+: Data Set Definition | Dset2, Dset3, Dset4, Dset5, Dset6, Dset7, Dset8, Dset9 DsetN1cd, DsetN2, DsetN3, DsetN4, DsetN5, DsetN6, DsetN7, DsetN8, DsetN9, DsetN10, DsetN11, DsetN12, DsetN13, DsetN14, DsetN15 |  |
| 3: Substitution | Sub1, Sub2, Sub3, SubN1 |  |
| 4: Setting Group Selection | Sg1, SgN1a | Sg3 |
| 4+: Setting Group Definition | Sg2, Sg4, SgN1b, SgN2, SgN3, SgN4, SgN5 |  |
| 5: Unbuffered Reporting | Rp1, Rp2, Rp3, Rp4, Rp7, Rp10, Rp12 RpN1, RpN2, RpN3, RpN4 | Rp5, Rp6, Rp8, Rp9, Rp11, RpN5, RpN6, RpN7 |
| 6: Buffered Reporting | Br1, Br2, Br3, Br4, Br7, Br8, Br9, Br12, Br14 BrN1, BrN2, BrN3, BrN4, BrN5 | Br5, Br6, Br10, Br11, Br13, BrN6, BrN7 |
| 6+: Enhanced buffered reporting | BrE1, BrE2, BrE3, BrE6, BrE7, BrE8, BrE9, BrE10, BrE11 | BrE4, BrE5, BrE12 |
| 9a: GOOSE publish | Gop2, Gop3, Gop4, Gop7, Gop10a | Gop1, Gop5, Gop6, Gop8, Gop9, Gop10b, GopN1, GopN2 |
| 9b: GOOSE subscribe | Gos1a, Gos2, Gos3, GosN1, GosN2, GosN3, GosN4, GosN5, GosN6 | Gos1b, Gos4 |
| 12a: Direct control | CtlN3, CtlN8 DOns1, DOns3 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 DOns2, DOns4, DOns5 |
| 12b: SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, SBOns2 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 SBOns3, SBOns4, SBOns5 |
| 12c: Enhanced Direct Control | CtlN3, CtlN8 DOes2, DOes5 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11 DOes1, DOes3, DOes4 |
| 12d: Enhanced SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, CtlN9 SBOes1, SBOes2, SBOes3 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11 SBOes4, SBOes5, SBOes6, SBOes7 |
| 13: Time sync | Tm1, Tm2, TmN1 | Tm3, TmN2 |
| 14: File transfer | Ft1, Ft2ab, Ft4, FtN1ab | Ft2c, Ft3, FtN1c |

[ All configuration file and data model tests have been successfully performed for the product variants using the same hardware and software version: <<Variant2>>, <<Variant3>> ]

# Comments

Does this need to be changed to refer to the PIXIT?