Test Procedures Change List (TPCL)

UCA IUG – Test Sub Committee

October 10, 2008

DRAFT

Introduction

This document specifies the changes to the server test procedures approved by the UCA IUG test sub committee. According to the QAP vendors have 1 year to implement changes resulting from new test procedures version. To be able to clarify conformance test procedures without changing the approved test procedures document the test sub committee have defined this "Test Procedures Change List".  Changes resulting in new test procedures shall be specified in the next revision of the test procedures.

This list:

- contains changes to the most recent test procedures

- indicate if a change is:

- Accepted, resulting in a clarified test procedure (included after the change list table)

- Denied

- Added to the next revision

- shall be used by recognized/accredited test labs

- should be referenced in the test report only

- is available at the sharepoint for test sub committee members

References

Conformance Test Procedures for Server Devices with IEC 61850-8-1 interface,

Revision 2.2, October 8, 2007

Change List

| ID | TEST CASE | CHANGE | FINAL PROPOSAL | RESULT |
| --- | --- | --- | --- | --- |
| 1 | Rp6 | Note in 7-2, $14.2.2.7 specifies that ConfRev may not change by using services on data sets. | Fix | Denied, the note should be removed |
| 2 | SubN1 | The testscript specifies changing value while subEna=T should fail. This is not specified in part 7-2 and this should be allowed | Update the test procedure | Agree, to clarify the test procedure |
| 3 | Br purge | Writing the same value to trgops, optflds etc should not purge the buffer (see part 8-1 just under table 37) | Add new test procedure for this | Next revision |
| 4 | RpN6, BrN6 | Response- error not specified | Expected Response- error should be “object-value-invalid” | Agree, to clarify the test procedure |
| 5 | Gop6 | Only GoEna is writable (part 8-1 table 50) | Remove the test steps with SetGoCBValues of other attributes | Agree, to clarify the test procedure |
| 6 | Sg | The SG last activation time is not tested at all. | Add new testcase to verify: 13.2.2.7 LActTm – last activation time The attribute LActTm shall identify the time when the last service SelectActiveSG has been processed. | Next revision |
| 7 | SBOes2 | Expected result still uses “CommandTermination” this should be “operate response-“ | Change the text. Shall we define AddCause = “parameter-change in execution” as well in case the operate ctlVal is differetn from the select ctlVal? | Agree, to clarify the test procedure |
| 8 | AssN4 | Detection of lost link Test Case (escpecially point 6.) ? The Test case description says the GetDataValues Response- is expected as response of "GetDataValues Request" after lost link. But there is no chance to get any response - the association is already aborted. | DUT sends no response” instead of “DUT sends GetDataValues Response- “ | Agree, to clarify the test procedure |
| 9 | CtlN10 | Next step after step c) is e). | Use d) | Agree, to clarify the test procedure |
| 10 | SgN3 | Ik kan het bestaansrecht van SgN3 niet terugvinden in de standaard. Bovendien klopt het script nu niet zoals beschreven in de procedure (die op zichzelf alweer zeer summier is). | Clarify SgN3, add reference to the standard |  |
| 11 | RpN4, BrN4 | RpN4 mentions the exact error codes, BrN4 not | Add error codes to BrN4 | Agree, to clarify the test procedure |
| 12 | Sub3 | A local function may undo the substitute values. Part7-2 page 64: There may be cases, where a local automatic function disables substitution, for example, if blocking of information exchange is disabled or communication is no longer interrupted. | Update test procedure. Add PIXIT entry to describe such function | Agree, to clarify the test procedure |
| 13 | DsetN15 | The condition RCB–RptEna=false is not tested | Add this check to the test: 1. Client requests a persistent CreateDataSet. 2. Client configures and enables a (buffered or unbuffered) RCB with this data set 3. Client requests a DeleteDataSet on the data set created in step 1 4. Client disables the RCB, repeat step 3 The expected result for step 4 is the same as for step 3 | Agree, to clarify the test procedure |
| 14 | Ft1 | Clarify the test cases expected result in case the GetServerDirectory(FILE) has no or empty parameters. As specified part 8-1 on page 39 "If the Filename (for instance MMS FileSpecification) is not present in the FileDirectory.request, then the responding server shall return the Filenames present in the root directory | Add or clarify the expected result when the request has no or empty filespecification parameter | Agree, to clarify the test procedure |
| 15 | CtlN4 | SBOns has no SelectWithValue | Replace SelectWithValue by Select | Agree, to clarify the test procedure |
| 16 | Gop3 | "First GOOSE sqNum at boot should be 1" according to Tissue 52. But 7-2 ed.2 CDV specifies: The initial value for SqNum upon a transition of GoEna to TRUE is recommended to be 0. | Update test procedure and allow any boot value of sqNum | Agree, to clarify the test procedure |
| 17 | CtlN3 | Vendors should be able to allow open command of the breaker, even if the position indicates open position. Motivation: Personal safety: e.g. in some cases the position indication sensor could be jammed and opening is needed. Technically XCBR.BlkOpn/BlkCls (or CILO.EnaOpn/EnaCls) should be used if the opening is not possible due to internal condition of the breaker (spring charging, disconnector state). Closing breaker could still be inhibited if the position indication indicates close. Part 7-2 17.2.2 does not directly inhibit above functionality but in conformance testing this functionality is not allowed | Remove CtlN3 or adjust the expected result as specified in PIXIT | Agree, to clarify the test procedure Adjust the expected result PIXIT |
| 18 | CtlN2 | Tissue 334 final proposal is to response- on second select; The testprocedures allows a positve respond | Update the testprocedure, the expected result is always negative | Agree, to clarify the test procedure |
| 19 | SBOns, DOns | The "red" IntOp Tissue 246 and 61850-8-1 ed2 CD table 57 are in conflict on Operate response- with or without an informationReport with LastApplError | Which one do we use as reference for the test? Will it be optional so we allow both? | Agree, to clarify the test procedure |
| 20 | Gos2 | Add the following situation: changing the test flag without changing the data and statenum. Same for NdsCom; Expected result should be described in the PIXIT: e.g. keep old state, set quality flag | Extend test case | Agree, next revision |
| 21 | CtlN1 | For SBOes a Operate response- is not a commandtermination but an information report | Replace command termination by InformationReport | Agree, to clarify the test procedure |
| 22 | Ctl3 and other | The expected result does not specify the AddCause and Error values | Specifiy other testcases as well. For Ctl3 the AddCause = "1-of-n control" with Error = Operate Test Not Ok | Agree, to clarify the test procedure Ctl3 |
| 23 | Ctl3 | Some devices allow only one control action simulaneously (1-of-n control). But other devices allow it as such these device send positieve respond! | Add reference to PIXIT if 1-of-n multi control is allowed or not | Agree, to clarify the test procedure |
| 24 | SBOes2 | Step expected result is not a commandtermination but a Operate respond- with informationreport | Replace commandtermination by operate respond- and informationreport | Agree, to clarify the test procedure |
| 25 | SBOns1, CtlN4b, CtlN2b | The expected result is incorrect; A select response- is mapped on read response+ with null value Note: by executing CtlN4 you also have performed SBOns1 as such the testcase could refer to CtlN4 | Expected result = DUT sends read response+ with Null value | Agree, to clarify the test procedure |
| 26 | Cnf5 | Ctlmodel should be initialized in SCD and CID, but for for ICD its conditional | Include the SCD/CID file as part of the test | Agree, to clarify the test procedure |
| 27 | Cnf6 | Configuration version is in SCD or CID not in ICD | Change ICD into SCD or CID | Agree, to clarify the test procedure |
| 28 | New | Add a testcase to verify the minimum supported IEDname+LD length is 32 chars |  | Agree, next revision |
| 29 | TICS template | Some "mandatory" tissues have changed | Update TICS template and annex C | Agree, to clarify the test procedure |

Clarified Test Procedures (in alphabetical order)

TBD