Test procedures for GOOSE performance according to IEC 61850-5 and IEC 61850-10 Version 1.1

On request of UCA International Users Group

Arnhem, April 14, 2010

| author : Richard Schimmel |  | reviewed : UCAIUG testsub |  |
| --- | --- | --- | --- |
| B 26 pages 2 annexes | RS | approved : UCAIUG testsub |  |

CONTENTS

page

1	Introduction	4

1.1	Test methodology	4

1.2	Test scope	6

1.3	Glossary	7

1.4	Identifications	8

2	Test environment	9

3	GOOSE performance testing	10

3.1	Message definitions	10

3.1.1	Published GOOSE used for ping-pong	10

3.1.2	Subscribed GOOSE used for ping-pong	11

3.1.3	Time correlated Subscribed GOOSE not used for ping-pong	12

3.1.4	Not subscribed GOOSE	12

3.1.5	Other communication tasks	13

3.2	Test cases	13

3.3	Test passed criteria	14

3.4	Test results	16

3.5	Detailed test procedure	17

Annex A 	Pixit Template For Goose Performance Test

Annex B 	Template For Goose Performance Test Certificate

# Introduction

The scope of the test is to benchmark the GOOSE performance of the DUT against the performance classes as defined in IEC 61850-5. IEC 61850-5 clause 13 states:

13.7.1.1 Type 1A “Trip” : The trip is the most important fast message in the substation. Therefore, this message has more demanding requirements compared to all other fast messages. The same performance may be requested for interlocking, intertrips and logic discrimination between protection functions.

- For Performance Class P1, the total transmission time shall be in the order of half a cycle. Therefore, 10 ms is defined.

- For Performance Class P2/3, the total transmission time shall be below the order of a quarter of a cycle. Therefore, 3 ms is defined.

IEC 61850-5 defines the transmission time as follows

Figure 1: Transmission time definition IEC 61850-5

## Test methodology

To measure the transmission time as defined in IEC 61850-5 is not possible without special access to the internal data of the device. To enable "black-box" testing a test lab needs a different test methodology referred to as the "GOOSE ping-pong" method. This method is already in use for GOOSE conformance testing.

Figure 2:	Measure round trip time using GOOSE ping-pong method

The GOOSE ping-pong method focuses on the round trip time as defined in figure 2. The round trip time is the time interval between the arrival of a subscribed GOOSE message and the departure of the published GOOSE message:  troundtrip = (ty – tx).

The relation between the transfer time and roundtrip time is as follows:

# ttransfer 				= ta + tb + tc

# troundtrip 	= (ty – tx)	= tc* + tapplication + ta*

When PD1 and PD2 are the same we assume that the GOOSE publish and subscribe  communication processing times are the same in figure 1 and 2. In that case we can combine these equations into:

- ttransfer = troundtrip – tapplication + tb

We assume the network delay for a single Ethernet switch to be minimal (< 0.1ms).  Then we get

- ttransfer = troundtrip – tapplication

ta 			= GOOSE publish communication processing

tb 			= network delay of one GOOSE message

tc 			= GOOSE subscribe communication processing

tapplication 	= application time

The application time typically is the sum of the scan cycle wait time and the actual application logic processing time. On a scan cycle of for example 4 ms the average scan cycle wait time is about 2 ms (50% of scan cycle). The measured maximum – minimum roundtrip times will be close to the scan cycle. These metrics can be used to perform a plausibility check on the documented figures in the PIXIT document.

# According to IEC 61850-10 a test system shall measure latency time by generating a sequence of physical/virtual input triggers to the IED and measuring the time delay to the corresponding message generated by the IED. The mean latency time and the standard deviation shall be computed across the responses to 1000 input triggers.

## Test scope

The following items may have an impact on the GOOSE performance:

- Size of the published/subscribed GOOSE message (number of data set elements)

- Type of data set elements

- Which element of the data set is used

- Use of Functionally Constrained Data (FCD) or Functional Constrained Data Attributes (FCDA) in the dataset

- Number of subscribed GOOSE messages

- Time correlation of subscribed GOOSE messages state changes

- Number of non-subscribed GOOSE messages on the network

- Other communication tasks like MMS reporting, file transfer and/or Sampled Values when supported

This test procedure is intended as a benchmark for comparing relative performance of different IEDs. It defines standardized tests aimed at mimicking typical workload conditions. It does not test device performance under worst case load, worst case network conditions, or in a specific system application. Please refer to detailed vendor specifications for full description of the device capabilities, behaviour and limitations.

## Glossary

BRCB		Buffered Report Control Block

DUT		Device Under Test

GoCB		GOOSE Control Block

GOOSE	Generic Object Oriented System Event

ICD		IED configuration description in SCL-format

IED 		Intelligent Electronic Device

FCD		Functionally Constrainted Data

FCDA		Functionally Constrainted Data Attributes

PICS		Protocol Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

MAC		Media Access Control

ms			milliseconds

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

UCAIUG	UCA International Users Group

URCB		Unbuffered Report Control Block

VLAN		Virtual Local Area Network

## Identifications

The following table gives the exact identification of tested equipment and test environment used for this performance test.

| DUT | <identification and short name of the device under test> <hardware and software version> Performance class: P1 or P2/P3 |
| --- | --- |
| MANUFACTURER | <name, location of the manufacturer of the DUT> |
| PICS | <complete reference description of the PICS> |
| PIXIT | <complete reference description of the PIXIT> |
| ICD or SCD | <complete reference description of the SCL configuration file> |
| TEST INITIATOR | <name and address of test initiator> |
| TEST FACILITY | <name and address of test facility> |
| TEST ENGINEER | <name and e-mail address of test engineer> |
| TEST SESSION | <date and location of the test session> |
| ANALYSER | <name and type analyzer(s), version X.Y> |
| GOOSE SIMULATOR | <name and type GOOSE simulator> |
| CLIENT SIMULATOR | <name and type client simulator> |
| TIME MASTER | <name and type of time master> |
| ETHERNET SWITCH | <name and type of Ethernet switch> |

The DUT shall be a regular production model. The only tuning that is allowed is ‘off-the-shelf’ configuration to minimize the application logic.

# Test environment

The test environment consists of the following components:

Figure 3: The test environment

The analyzer compares the published and the subscribed GOOSE messages from the DUT.

The client simulator simulator is used to simulate specific communication during the test.

The DUT shall not be reconfigured during the performance test. The test procedures are designed in such a way that the DUT doesn't need to be reconfigured during the performance test.

# GOOSE performance testing

## Message definitions

The general message requirements are:

- Each GOOSE has unique multicast destination MAC address

- Each GOOSE has VLAN priority = 4 and VLAN ID = 0

- Each GOOSE has Test = FALSE, NdsCom = FALSE

- The GOOSE datasets contain functionally constrained data attributes (FCDA)

- The BRCB or URCB datasets contain functionally constrained data (FCD)

### Published GOOSE used for ping-pong

The DUT will publish the following GOOSE:

Dataset					normal dataset = 4 Boolean data values and 4 qualities

Structure normal dataset:

(bool1, q1, bool2, q2, bool3, q3, bool4, q4)

large dataset = 20 Double Point data values, 20 Boolean Data values and 40 qualities

Structure large dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema	Given by subscribed GOOSE, retransmission scheme as specified in the DUT documentation

GoCB name				GPFPPpongNormal, 			GPFPPpongLarge

Dataset name	GPFPPpongNormal 			GPFPPpongLarge

Destination MAC			0x01 0C CD 01 00 01, 		0x01 0C CD 01 00 02
APPID						3001							3001

### Subscribed GOOSE used for ping-pong

The DUT will subscribe to the following GOOSE:

Dataset					normal dataset = 4 Boolean data values and 4 qualities

Structure normal dataset:

(bool1, q1, bool2, q2, bool3, q3, bool4, q4)

large dataset = 20 Double Point data values, 20 Boolean Data values and 40 qualities

Structure large dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema	4 state changes of the last data value element per second (about each 250 ms) uniform distributed over the scancycle

Retransmission at 4 and 32 ms (or more)

GoCB name				GPFPPpingNormal, 			GPFPPpingLarge

GocbRef	GPFPPpingNormalLD0/LLN0$GO$GPFPPpingNormal GPFPPpingLargeLD0/LLN0$GO$GPFPPpingLarge

Dataset name				GPFPPpingNormal 			GPFPPpingLarge

Destination MAC			0x01 0C CD 01 00 03			0x01 0C CD 01 00 04

APPID						3001							3001

### Time correlated Subscribed GOOSE not used for ping-pong

The DUT will also subscribe to the following GOOSE:

Dataset	large dataset = 20 Double Point data values, 20 Boolean data values and 40 qualities

Structure of dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema		5 subscribed GOOSE control blocks

Retransmission at 4, 32 and 256 ms (or more)

5 subscribed GOOSE each having one state change of the 5th data value element at approxamatly -4.0, -2.0, 0.0, 2.0 and 4.0 ms before and after the subscribed GOOSE state change used for ping-pong The 5 GOOSE control blocks are published by 5 IED’s (each one publishing 1 GOOSE control block.

GocbRef	GPFsubscribed1..5LD0/LLN0$GO$GPFsubscribed1..5

Dataset name	GPFsubscribed1..5

Destination MAC	0x01 0C CD 01 00 05 to 0x01 0C CD 01 00 09

APPID	3001							3001

### Not subscribed GOOSE

Dataset	large dataset = 20 Double Point data values, 20 Boolean data values and 40 qualities

Structure of dataset:

(bool1, q1, bool2, q2, …., bool20, q20, DP1, q1, DP2, q2, ….,DP20, q20)

Transmission schema	100 GOOSE control blocks each with 1 state change per second (about every 10 ms) and 2 retransmissions per second (at 32 and 256 ms or more). The total number of these GOOSE messages will be at least 300 messages per second. The 100 GOOSE control blocks are published by 20 IED’s (each one publishing 5 GOOSE control blocks.

GocbRef				GPFnotSubscribed001..100LD0/LLN0$GO$GPFnotSubscribed001..100

Dataset name				GPFnotSubscribed001..100

Destination MAC	0x01 0C CD 01 11 01    to    0x01 0C CD 01 11 64

APPID7	3001							3001

### Other communication tasks

In case the DUT supports reporting one client shall be connected to the DUT during all test cases. The client enables two BRCBs or when buffered reporting is not supported two URCBs with same data values (as FCD) as the normal and large dataset in the published GOOSE. The report control blocks shall be configured to send reports on data change and quality change with all supported optional fields.

## Test cases

The following table gives an overview of the test cases.

| Test ID | Subscribe (ping) | Publish (pong) | Time correlated Subscribed GOOSE not used for ping-pong | Not subscribed |
| --- | --- | --- | --- | --- |
| Gpf1 | Normal | Normal | No | No |
| Gpf2 | LARGE | LARGE | No | No |
| Gpf3 | Normal | Normal | YES | No |
| Gpf4 | Large | Large | Yes | No |
| Gpf5 | Normal | Normal | No | YES |
| Gpf6 | LARGE | LARGE | No | YES |
| Gpf7 | Normal | Normal | YES | YES |
| Gpf8 | LARGE | LARGE | YES | YES |

Note: "No" means that the GOOSE simulator will not publish GOOSE message, because they are not relevant for this test case.

## Test passed criteria

For performance class P1 the transmission limit is defined as 10 ms and 3 ms for P2/P3. According to IEC 61850-10 clause 7.2.1 the performance results are the average and standard deviation over 1000 input triggers and that the sum of the measured output and input latency shall be less than or equal to 80 % of the total transmission (because 20% is reserved for network latency).

In clause 1.1 we determined:  ttransfer = troundtrip – tapplication. The application time typically is the sum of the internal scan cycle wait time and the actual logic processing time. To represent  the worst case transfer time we set the actual logic processing time to zero (this means that the logic processing time is considered as part of the transfer time). As a result we get:

- Average application time 		=   50% of scan cycle

- Maximum application time 	= 100% of scan cycle

- Minimum application time 	=     0% of scan cycle

Now the transfer time can be calculated as follows:

- Average:	ttransfer.avg = troundtrip.avg – tapplication.avg 	= troundtrip.avg – scancycle/2

- Maximum:	ttransfer.max = troundtrip.max – tapplication.max 	= troundtrip.max – scancycle

- Minimum:	ttransfer.min = troundtrip.min – tapplication.min 	= troundtrip.min

Note: it is possible that the calculated maximum transfer time is less than the calculated minimum transfer time.

Plausibility checks:

- Documented scan cycle ≥ Measured scan cycle = troundtrip.max – troundtrip.min

- Documented scan cycle ≥ Measured standard deviation * 3.46   (for uniform distribution)

In case the measured scan cycle is more than the documented scan cycle, the documented scan cycle shall be adjusted. In case the DUT has an event driven method (no scan cycle) the scan cycle for the calculations is set to 0.0 ms.

To pass the performance test the criteria are:

- Gpf1 to Gpf6 test are passed when the calculated average, maximum and minimum transfer times are less than 80% of the applicable performance class limit (IEC 61850-10 clause 7.2.1 Note 1):

  - Performance class P1; 		ttransfer < 8.0 ms

  - Performance class P2/P3; 	ttransfer < 2.4 ms

- Gpf7 and Gpf8 test is passed when the average, maximum and minimum calculated transfer times are less than 100% of the performance class limit:

  - Performance class P1; 		ttransfer <10.0 ms

  - Performance class P2/P3; 	ttransfer <  3.0 ms

The PIXIT document shall specify the GOOSE performance class and application logic scan cycle(s).

The DUT has passed the GOOSE performance test when all test cases are passed.

## Test results

Documented scan cycle 	= x.y ms

Measured scan cycle 		= x.y ms

Performance class 		= P1 or P2/P3

| Test ID | Minimum | Maximum | Average | Verdict |
| --- | --- | --- | --- | --- |
|  |  | Round-trip | Transfer | Round-trip | Transfer | Stddev |  |
| Gpf1 | x.y | x.y | x.y | x.y | x.y | x.yy | Passed |
| Gpf2 | x.y | x.y | x.y | x.y | x.y | x.yy | Failed |
| Gpf3 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf4 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf5 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf6 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf7 | x.y | x.y | x.y | x.y | x.y | x.yy |  |
| Gpf8 | x.y | x.y | x.y | x.y | x.y | x.yy |  |

## Detailed test procedure

| Gpf1 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf1 = with normal Subscribe (ping) |
| Comment Gpf1 transfertimemax = |

| Gpf2 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf2 = with large Subscribe (ping) |
| Comment Gpf2 transfertimemax =.. Any deviation to Large Dataset structure as defined? |

| Gpf3 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf3 = with normal Subscribe (ping) & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf3 transfertimemax = |

| Gpf4 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf4 = with large Subscribe (ping) & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf4 transfertimemax = Any deviation to Large Dataset structure as defined? |

| Gpf5 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf5 = with normal Subscribe (ping) & not subscribed GOOSE |
| Comment Gpf5 transfertimemax = |

| Gpf6 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf6 = with large Subscribe (ping) & not subscribed GOOSE |
| Comment Gpf6 transfertimemax = Any deviation to Large Dataset structure as defined? |

| Gpf7 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf7 = with normal Subscribe (ping) & not subscribed GOOSE & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf7 transfertimemax = |

| Gpf8 | GOOSE performance tests | ( Passed ( Failed |
| --- | --- | --- |
| IEC 61850-5 clause 13 |
| Expected result 4. The device publishes GOOSE pong messages with copied values 7. According to paragraph "3.3 Test passed criteria" |
| Test description 1. Configure and start DUT 2. Client simulator associates with DUT, configures and enables the BRCB or URCB 3. Start high performance analyzer capture 4. Start GOOSE simulator as indicated below 5. Wait for 1000 uniform distributed Subscribe (ping/pong) state changes 6. Stop and save the analyzer capture 7. Calculate the 1000 roundtrip times and calculate the average, minimum, maximum roundtrip time and standard deviation Gpf8 = with large Subscribe (ping) & not subscribed GOOSE & time correlated Subscribed GOOSE not used for ping-pong |
| Comment Gpf8 transfertimemax = Any deviation to Large Dataset structure as defined? |

ANNEX A: PIXIT template for GOOSE performance test

Introduction

This document specifies the protocol implementation extra information for testing (PIXIT) of the IEC 61850 GOOSE performance in the server device:  “<product>” with version “<version>”.

Together with the PICS this PIXIT forms the basis for a GOOSE performance test according to IEC 61850-5 and IEC 61850-10.

PIXIT for GOOSE performance test

| Description | Value / Clarification |
| --- | --- |
| Performance class | P1 or P2/P3 |
| GOOSE ping-pong processing method | Event driven based or Scan cycle based |
| Application logic scan cycle(ms) |  |
| Maximum number of Goose Dataset entries (value and quality has to be counted as separate entries) | 50 |
| Maximum number of Goose Control Blocks to be published | 5 |
| Maximum number of Goose Control Blocks to be subscribed | 50 |
| Data types supported to publish Goose | Boolean / Double Point / Analog |
| Data types supported to subscribe Goose | Boolean / Double Point / Analog |

ANNEX B: Template for GOOSE performance test certificate

IEC 61850 Certificate Level A/B1

| Issued to: | For the product: |
| --- | --- |
| <<MANUFACTURER>> << FULL ADDRESS>> | <<PRODUCT NAME>> <<VERSION NUMBER>> |

Issued by:  << TEST LAB >>

# The product has not shown to be non-conforming to:

IEC 61850-5 performance class <<P1 or P2/P3>>

The performance test has been performed according to the UCA International Users Group GOOSE performance Test Procedures version X.Y with product’s protocol implementation conformance statements: “<<PICS>>”, and product’s extra information for testing: “<<PIXIT>>”.

This Certificate summaries test results as carried out at <<TESTLAB>> in <<COUNTRY>> with <<GOOSE simulator VERSION>> and <<Analyzer VERSION>>. This document has been issued for information purposes only, and the original paper copy of the test report: No. <<REPORT NUMBER>> will prevail.

The GOOSE performance has been measured with <<Boolean and/or Double Point>> informations.

<<LOCATION>>, <<DATE>>

<<Signature of responsible test engineer>>

<<Name of responsible test engineer>>

# 1 Level A - Independent Test lab with certified ISO 9000 or ISO 17025 Quality System

# Footnotes

In case the DUT does not support 20 Boolean or 20 DP, or the DUT has some limitations regarding dataset size, the LARGE Dataset shall contain at least 40 values and 40 qualities or the maximum number of dataset entries that is possible according to the description in PIXIT.

By using the names defined in the test procedures the analyzing of the capture files would be much easier, but the names have no impact to the performance. So alternative names are allowed

The APPID shall be the same for all GOOSE Messages during the Tests but the value it self can be different as defined above in case there are some limitation related to the DUT

In case the DUT does not support 20 Boolean or 20 DP, or the DUT has some limitations regarding dataset size, the LARGE Dataset shall contain at least 40 values and 40 qualities or the maximum number of dataset entries that is possible according to the description in PIXIT.

By using the names defined in the test procedures the analyzing of the capture files would be much easier, but the names have no impact to the performance. So alternative names are allowed.

The APPID shall be the same for all GOOSE Messages during the Tests but the value it self can be different as defined above in case there are some limitation related to the DUT

The APPID shall be the same for all GOOSE Messages during the Tests but the value it self can be different as defined above in case there are some limitation related to the DUT

http://en.wikipedia.org/wiki/Uniform_distribution_(continuous)

# Comments

As discussed in Paris we should start to migrate the test procedure documents to UCA format. No references to other companies. References to the authors shall remain.

We shall verify the correctness of this statement. As such we need to keep the non-subscribed GOOSE message testcase (removed at the previous telco)

I think it depends on the implementation on the IED. In case of an proper implementation and dataflow engineering it has no influence, but would be interesting to verify it.

ConfRev has no impact to performance, but will be set automatically by some Engineering tools during the preparation of the configuration on the DUT. That’s why ConfRev shall be removed.

The structure of the datasets has to be described.

The structure of the datasets has to be described. Otherwise it is not clear witch type of Dataset entry will be used for Ping-Pong.

The Goose ID shall not be mentioned because it doesn’t matter. And is in most IED’s the reference to the dataset by default

On the end the APPID should have no impact to the performance, because we have unique Mac Addresses and the Mac Addresses filtering will sort out Goose Messages that are not to be subscribed before the DUT can analyze any APPID (Application identifier). Anyhow to verify the proper implementation. I know that some vendors have also only a limited ranch for the APPID available. Therefore footnote 3

The Structure of the datasets has to be described.

The structure of the datasets has to be described. Otherwise it is not clear witch type of Dataset entry will be used for Ping-Pong.

The last dataset elemet need’s most properly most time to get processed

The Goose ID shall not be mentioned because it doesn’t matter. And is in most IED’s the reference to the dataset by default

See SG8

The Structure of the datasets has to be described.

Could not be exactly measured caused by buffer handlings on IED’s and switches. The state changes issuing  retransmissions as well. The focus shall not be on the exact time correlation to the ping-pong GRCB’s it should be on the load.

I think it will be a more realistic case then the Goose are distributed from several IED’s (for example 5 IED’s each one with 1 GCB).

The Goose ID shall not be mentioned because it doesn’t matter. And is is most IED’s the reference to the dataset by default.

See SG8

The Structure of the datasets has to be described.

I think it will be a more realistic case then the Non Subscribed Goose are distributed from several IED’s

The Goose ID shall not be mentioned because it doesn’t matter. And is in most IED’s the reference to the dataset by default.

See SG 8.

To use integrity as trigger option is no realistic usecase.

I would expend the test cases as follow, so we test each combination (Gpf 4,6 and 7 are added). In case an supplier does not support Double Point all test will be done with Bolen (Normal an Large Dataset)!

Subscribe Errors on DUT shall not influence the performance for proper subscribed and published Goose Messages, so there should be no impact, but facilitates the whole test.

In case the DUT does not support the Large dataset structure as defined, the configured dataset structure shall be documented here.

In case the DUT does not support the Large dataset structure as defined, the configured dataset structure shall be documented here.

In case the DUT does not support the Large dataset structure as defined, the configured dataset structure shall be documented here.

In case the DUT does not support the Large dataset structure as defined, the configured dataset structure shall be documented here.

I would suggest as well to keep the Certificate as simple as possible and not to mention on the certificate any measured results. We should just indicate which Performance class according to part 10 is reached by the DUT.
The detailed measurements shall be documented in the Test report only.

# Text boxes

KEMA Nederland B.V.  Utrechtseweg 310, 6812 AR Arnhem  P.O. Box 9035, 6800 ET Arnhem  The Netherlands

T +31 26 3 56 91 11  F +31 26 3 89 24 77  contact@kema.com  www.kema.com  Registered Arnhem 09080262

This document  may be distributed to UCA international users group members only.

High Performance Analyzer

GOOSE Simulator

Device Under Test

Ethernet Switch

Client Simulator

tx

ty

troundtrip

Physical device PD1

Application Logic to

copy value

Communication processor

subscribed GOOSE messages

published GOOSE messages

Time Master

ta*

tapplication

tc*