30101082-Consulting 10-version0.1

Test procedures for Sampled Values Subscribers according to the "Implementation Guideline for Digital Interface to Instrument Transformers using IEC 61850-9-2" (9-2LE) Version 0.1

On request of UCAIUG

June 8, 2010

Author Richard Schimmel

KEMA Consulting

| author : Richard Schimmel | <date> | reviewed : Bruce Muschlitz | <date> |
| --- | --- | --- | --- |
| B 28 pages 2 annex | RS | approved : Jack Robinson | <date> |

Revision history

| Version | Changes |
| --- | --- |
| 0.1, June 8, 2010 | Initial version |

CONTENTS

page

1	Introduction	5

1.1	Glossary	5

1.2	Identifications	6

2	Test environment	7

3	Test results	8

4	Conclusion and recommendations	9

4.1	Recommendations following from the test	9

5	Test procedures for 9-2LE publishers	10

5.1	Documentation	10

5.2	Configuration	10

5.3	Communication services	11

5.3.1	Abstract test cases	11

5.3.2	Detailed test procedures	13

Annex A	PIXIT FOR 9-2LE PUBLISHER	14

ANNEX B 	9-2LE SubSCRIBer Certificate Form	16

# Introduction

The scope of the test is an IED subscribing IEC 61850-9-2 sampled value messages constrained by the 9-2LE guideline. For example such IED could be a protection relay or meter.

The test procedures in this document are based on the "Implementation Guideline for Digital Interface to Instrument Transformers using IEC 61850-9-2, version 2.1, July 2004" further referred to as 9-2LE.

Note: In case a 9-2 subscribing IED supports GOOSE or MMS based services to transfer binary status or control indications the applicable server conformance test procedures version 2.2 have to be used for the test

## Glossary

DUT		Device Under Test

ICD		IED configuration description in SCL-format

IED		Intelligent Electronic Device

MICS		Model Implementation Conformance Statement

MU			Merging Unit

PICS		Protocol Implementation Conformance Statement

TICS		Technical Issues Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

PPS		Pulse Per Second

PTP		Precision Time Protocol

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

TISSUE	Technical issue

UCAIUG	UCA International Users Group

## Identifications

The following table gives the exact identification of tested equipment and test environment used for this conformance test.

| DUT | <identification and short name of the device under test, type, hardware / software version> Supported sampling rates: 80 and/or 256 samples per cycle Supported frequencies: 50Hz and/or 60Hz |
| --- | --- |
| MANUFACTURER | <name, location of the manufacturer of the DUT> |
| PICS | <complete reference description of the PICS> |
| MICS | <complete reference description of the MICS> OR reference to 9-2LE |
| TICS | <complete reference description of the TICS> OR reference to 9-2LE |
| PIXIT | <complete reference description of the PIXIT> |
| ICD or SCD | <complete reference description of the SCL configuration file> |
| TEST INITIATOR | MANUFACTURER |
| TEST FACILITY | <name and address of test facility> |
| TEST ENGINEER | <name and e-mail address of test engineer> |
| TEST SESSION | <date and location of the test session> |
| ANALYSER | <name and type analyzer(s), version X.Y> |
| SIGNAL GENERATOR | <name and type equipment simulator> |
| TIME MASTER | <name and type of time master> |
| MEDIA CONVERTERS | <name and type of media converters> |

# Test environment

The test environment consists of the following components:

•	DUT = 9-2LE subscriber

•	SV signal generator

•	SV Analyzer

•	Ethernet switch

•	time master (not in picture)

Figure 2.1 The test environment

The SV signal generator shall be accurate enough to perform the accuracy plausibility tests.

# Test results

Table 3.1 in this Chapter gives an overview of the conformance test results. References shown in the table columns refer to references of individual test procedures in clause 5.

The Mandatory column indicates the mandatory test cases with test result passed and the Conditional column indicates the conditional test cases with test result passed.

The Verdict column indicates the test result of all applicable test procedures in the test group. When one or more test procedures have test result Failed the test group receives verdict Failed.

Table 3.1	Overview of applicable test cases for DUT

| Test Group | Mandatory | Conditional | Verdict |
| --- | --- | --- | --- |
| Documentation | Doc1, Doc2 |  |  |
| Configuration |  |  |  |
| 11b Sampled Value Subscribing 50 Hz, 80 samples/cycle |  |  |  |
| 11b Sampled Value Subscribing 60Hz, 80 samples/cycle |  |  |  |
| 11b Sampled Value Subscribing 50 Hz, 256 samples/cycle |  |  |  |
| 11b Sampled Value Subscribing 60Hz, 256 samples/cycle |  |  |  |

# Conclusion and recommendations

Based on the test results described in this report, TEST FACILITY declares the tested IEC 61850 implementation in the DUT has [not shown/shown] to be non-conforming to 9-2LE as specified in the PICS, MICS, PIXIT, TICS and ICD and configured according to the SCD.

## Recommendations following from the test

The following comments and recommendations apply for the DUT:

<comments and recommendation from test facility>

# Test procedures for 9-2LE publishers

## Documentation

| Id | Test procedure | Verdict |
| --- | --- | --- |
| Doc1 | Check if the manufacturer documentation and hardware / software versions of the DUT do match: PICS MICS (reference to 9-2LE) PIXIT TICS (reference to 9-2LE) Hardware/software versions match |  Passed  Failed  Inconclusive |
| Doc2 | Verify the PIXIT matches the PIXIT template from the test procedures document |  Passed  Failed  Inconclusive |

## Configuration

| Id | Test procedure | Verdict |
| --- | --- | --- |
| Cnf1 | Verify the DUT can be configured with SCD. DUT shall subscribe to the SV as specified |  Passed  Failed  Inconclusive |
| Cnf2 | Verify the DUT can subscribe to an MU with the maximum IED name (SvID) length |  Passed  Failed  Inconclusive |
| Cnf3 |  |  Passed  Failed  Inconclusive |

## Communication services

Only supported system frequencies and sampling rates shall be tested.

### Abstract test cases

Positive test cases

| Test ID | Test Case | M/C |
| --- | --- | --- |
|  | Verify that physical layer is 100Base-FX full duplex with ST or MT-RJ connectors or 100Base-TX with RJ45 connector (PIXIT) | M |
|  | Verify that the MSVCB01 samples are subscribed with 80 messages per cycle; for one and max number of merging units | C1 |
|  | Verify that the MSVCB02 samples are subscribed with 32 (256/8) messages per cycle; for one and max number of merging units | C1 |
|  | Verify that the DUT subscribes to SV with 1ms, 2ms and 3ms rated delay time | M |
|  | Verify that the sampled values are translated into RMS Volt and Amp values (plausibility) | C2 |
|  | Verify that the DUT is synchronised with time synch signal | M |
|  | Verify that after restoring the power the DUT is subscribing valid 9-2 messages within specified time (PIXIT). | M |
|  | Verify the behavior of the DUT when the quality bit TEST is set for each sample (PIXIT) in one and all merging unit | C3 |
|  | Verify the behavior of the DUT when the quality bit INVALID is set for each sample in one merging unit (PIXIT) | M |

Conditions

C1 = at least 80 or 256 sample rate shall be supported C2 = mandatory in case DUT can 'present' the calculated RMS values C3 = mandatory in case TEST mode is supported

NOTE: Svs5 - shall we verify the plausibility of the kWh meter values as well?

Negative test cases

| Test ID | Test Case | M/C |
| --- | --- | --- |
|  | Verify DUT behaves as specified in PIXIT when all SV from one merging unit are missing |  |
|  | Verify DUT behaves as specified in PIXIT when 1, 10, 100, 1000, 10000 samples from one merging unit are missing |  |
|  | Verify DUT behaves as specified in PIXIT when the SV header in one merging unit contains a mismatching: - MAC address - Ethertype <> 0x88BA - SvID - ConfRev - APPID <> 0x4000 - Reserved fields <> 0x0000 |  |
|  | Verify DUT behaves as specified in PIXIT when all Volt and/or Amp samples change the quality to invalid and back to valid again |  |
|  | Verify that the DUT behaves a specified in the PIXIT when it subscribes to SV with 5ms and 10ms rated delay time |  |
|  | Verify that the DUT behaves a specified in the PIXIT when the time synch signal is lost and restored again for: - one MU - all MU - in DUT - in all MU and DUT |  |

### Detailed test procedures

TBD

##### Annex A	PIXIT FOR 9-2LE PUBLISHER

| Description | Value / Clarification |
| --- | --- |
| Supported nominal frequencies? | 50 Hz Y/N 60 Hz Y/N |
| Supported sampling rates? | 80 samples per cycle Y/N 256 samples per cycle Y/N |
| 9-2 connector type? | ST, MT-RJ and/or RJ45 |
| Input voltage and currents signals | 0, 1, 3 or 4 phase voltages 0, 1, 3 or 4 phase currents |
| Maximum number of SV streams? | …. SV streams V and A combined …. SV streams V and A in separate stream |
| Max length for SvID? | Max length of SvID = 32 |
| What is the maximum acceptable (rated) delay time between taking the sample and receiving the corresponding SV message? | … milliseconds (> 3 milliseconds) |
| Which quality codes are supported? | Derived Y/N Test Y/N |
| The DUT supports the following methods to indicate a subscribe failure: - LED indication on front panel - IEC 61850 data point - add event to internal log - output contact - other | Y/N Y/N, available by GOOSE or report Y/N Y/N <describe, to be agreed by test lab> (note: one method is mandatory) |
| Does the subscriber supports test mode? | Y/N |
| What is the behavior of the DUT when SV required data is received with quality=test? |  |
| What is the behavior of the DUT when SV required data is received with quality = invalid? |  |
| What is the behavior of the DUT when only a number (1-10-100) of required SV samples are missing? |  |
| What is the behavior of the DUT when a number of required SV samples are delayed beyond the maximum acceptable delay time? |  |
| At losing the timesynch signal after how much time this is detected by the DUT? | … seconds |
| At restoring the timesynch signal after how much time sets this is detected by the DUT? | … seconds |
| What is the behavior of the DUT when the timesynch signal is lost: - in one of the merging units? - in all subscribed merging units? - in the DUT? - in all merging units and DUT |  |
| Which values are verified to subscribe to an SV stream? And what is the behavior of the DUT when a the verification fails? | MAC address Ethertype APPID Reserved fields 1 and 2 SvID ConfRev |
| What is the typical startup time after a power supply interrupt? | … seconds |
| <additional items> |  |

##### ANNEX B 9-2LE SubSCRIBer Certificate Form

The template form for certificates issued upon completion of device testing is as follows:

# Text boxes

T +31 26 356 9111  F +31 26 351 3683   contact@kema.com  www.kema.com  Registered Arnhem 09080262

Copyright © KEMA Nederland B.V., Arnhem, the Netherlands. All rights reserved.

This document  may be distributed to UCA international users group members only.

KEMA Nederland B.V. and/or its associated companies disclaim liability for any direct, indirect, consequential or incidental damages that may result from the use of the information or data, or from the inability to use the information or data.

.

| No. <document reference> | IEC 61850 Certificate Level A/B1 |
| --- | --- |
| Issued to: | Page 1/2 For the 92LE subscriber: |
| <Name and Address> | <device> <Hardware version> <Firmware version> Supporting: 1/3/4 phase voltage and/or current from XXX sources |

Issued by:  <testlab>

# The product has not shown to be non-conforming to:

## IEC 61850-6, 7-2 and 9-2

### Communication networks and systems in substations

The conformance test has been performed according to IEC 61850-10 with 92LE publisher’s protocol implementation conformance statement: “<PICS PIXIT>” and extra information for testing: “<PIXIT>”.

The following IEC 61850 conformance blocks have been tested with a positive result (number of relevant and executed test cases / total number of test cases as defined in the UCAIUG Test procedures for Sampled Values Subscribers according to the "Implementation Guideline for Digital Interface to Instrument Transformers using IEC 61850-9-2" (9-2LE), version x.x):

| 11a Sampled Value Subscriber (X/Y) | 50 Hz with 80 samples per cycle |
| --- | --- |
| 11a Sampled Value Subscriber (X/Y) | 60 Hz with 80 samples per cycle |

This Certificate includes a summary of the test results as carried out at <location> with <Analyzer version>. The test is based on the UCAIUG “Test procedures for Sampled Values Subscribers according to the "Implementation Guideline for Digital Interface to Instrument Transformers using IEC 61850-9-2" (9-2LE), version x.x”. This document has been issued for information purposes only, and the original paper copy of the test report: No. <document reference> will prevail.

The test has been carried out on one single specimen of the client system as referred above and submitted to <testlab> by <manufacturer>. The manufacturer’s production process has not been assessed. This Certificate does not imply that <testlab> has certified or approved any product other than the specimen tested.

<Location & date>

<manager name>	<name>

<tiltle>	<Test Engineer>

# 1 Level A - Independent Test lab with certified ISO 9000 or ISO 17025 Quality System

Page 2/2

Applicable Test Procedures from the UCAIUG "Test procedures for Sampled Values Subscribers according to the "Implementation Guideline for Digital Interface to Instrument Transformers using IEC 61850-9-2 (9-2LE)", version x.x”

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| Configuration | tbd | tbd |
| 11b Sampled Value Subscribing 50 Hz, 80 samples/cycle | tbd | tbd |
| 11b Sampled Value Subscribing 60 Hz, 80 samples/cycle | tbd | tbd |
| 11b Sampled Value Subscribing 50Hz, 256 samples/cycle | tbd | tbd |
| 11b Sampled Value Subscribing 60Hz, 256 samples/cycle | tbd | tbd |

or

V

V+A

SV Analyzer

Client Simulator

(optional)

SV

Generator

Managed Ethernet Switch

9-2LE subscriber with 1 or 2 network interfaces