30800601-Consulting 08-version0.3

Test procedures for IEC 61850-9-2 publisher DRAFT 0.3

On request of UCAIUG

December 8, 2008

Author Richard Schimmel

KEMA Consulting

| author : Richard Schimmel | 22-10-08 | reviewed : Edwin Melenhorst | 22-10-08 |
| --- | --- | --- | --- |
| B 8 pages 2 annexes | RS | approved : Willem strabbing | 22-10-08 |

CONTENTS

page

1	Introduction	4

2	Test procedures for 9-2LE publisher	5

# Introduction

The scope of the test is an IED publishing IEC 61850-9-2 sampled value messages constrained by the 9-2LE guideline. For example such IED could be a Merging Unit. A merging unit is a device that converts analog input signals from one or more CT's and VT's and merges the samples into a digital IEC 61850-9-2 sampled value message.

The test procedures in this document are based on the "Implementation Guideline for Digital Interface to Instrument Transformers using IEC 61850-9-2, version 2.1, July 2004" further reffered to as 9-2LE.

The following table specifies which test procedures are mandatory/conditional for the conformance block.

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 11a Sampled values part 9-2 publish | SvpX | <condition>: SvpY |
| 11b Sampled values part 9-2 subscribe | Future (SvsX) | Future (SvsY) |

Note: In case a 9-2 publishing IED supports GOOSE or MMS based services to transfer binary status or control indications the applicable server test procedures version 2.2 has to be used for the conformance test

# Test procedures for 9-2LE publish

Documentation

- PICS – compare template in IEC 61850-9-2 $9.2 (the F/S columns may be removed)

- MICS – as defined in 9-2LE, just refer to 9-2LE

- TICS – as defined in 9-2LE, just refer to 9-2LE

- PIXIT – template will be included in the test procedures

All documents shall mention the device name and versions. For practical reasons the documents may be integrated in one document.

Configuration

- ICD file – compare example in 9-2LE

- SCD, CID file or table 10 in 9-2LE:

| Parameter | Value Range | Comment / SCL configuration |
| --- | --- | --- |
| LDName | xxxxMUnn | xxxx is, according to [6], clause 8.4.2, the concatenation of substation name, voltage level and bay MUnn is, according to [6] the attribute Inst of the element LDevice. MU is predefined by this standard while nn needs to be configured and is used to differentiate several merging units within the same bay; i.e. nn identifies the measuring point. |
| MACDestinationAddress for MSVCB01 | 01-0C-CD-04-xx-xx | xx-xx needs to be configured if MSVCB01 is enabled |
| MACDestinationAddress for MSVCB02 | 01-0C-CD-04-xx-xx | xx-xx needs to be configured if MSVCB02 is enabled |
| MSVCB01 Enabled | TRUE/FALSE | Transmission of 80 samples per nominal line cycle enabled |
| MSVCB02 Enabled | TRUE/FALSE | Transmission of 256 samples per nominal line cycle enabled |
| Nominal frequency | ENUMERATION (50, 60, …) | Values like 16.7 or 25 may be used in the future |

Note: if the device does not supply all samples, ‘dummy’ SAV data objects might be referenced in the data set.  To detect the difference between dummy and real samples in the ICD/SCD,  the ICD shall have all LN's included but the ones that are not supported have the LN Mode preconfigured to "Off".

Samples that are not measured or calculated shall have Quality bit = Invalid. In case an analog input signal is not connected or temporarely broken the corresponding Quality field shall toggle from Invalid <> Valid.

Communication services

Chapter 5 USE OF IEC 60044-8

- The maximum delay time as specified in clause 5.3.2, NOTE 2 shall apply as maximum allowed delay.   FST: The delay specified is for the whole transmission path. The MU must be "faster" to allow some margin for the time used in the network. But to my knowledge, there is no spec for the delay of the MU alone.

- The specification of the clock input according to clause 6.2.5 of [44-8] shall apply as well.

Chapter 6 USE OF IEC 61850-9-2

- 6.1:    SendMSVMessage is Mandatory

- 6.2.1: Physical layer = Verify 100Base-FX full duplex with ST or MT-RJ connectors or 100Base-TX with RJ45

- 6.2.2: Link layer = Verify that the APPID is 0x4000  (fixed by 9-2LE)

- 6.2.3: Verify that the Quality attribute of the calculated samples is extended with the "derived" bit

7 SPECIFICATION OF THE LOGICAL DEVICE "MU"

7.1

- Verify the name and logical nodes of the logical device xxxxMUnn (table 4) in the SCL

- Verify the logical node LLN0 of the logical device xxxxMUnn (table 5) in the SCL

- Verify the dataset PhsMeas1 (table 6) in the SCL

- Verify the common data class SAV and scalefactor values (table 7) in the SCL

- Verify the Multicast sampled value control block "MSVCB01" and/or "MSVCB02" (table 8 and table 9) in the SCL

- Verify the SCL configuration matches with the configuration data in the sampled values messages (svID "xxxxMUnn01" matches the name and logical device)

7.2

Possible operating modes are

ON 	publish 9-2 messages

TEST 	messages with test flag, optional, behavior as specified in PIXIT (the test flag is one bit in the quality field)

OFF 	during startup, no messages

After restoring the power the IED shall publish 9-2 messages within specified time (PIXIT).

Verify the IED supports a 1 PPS type signal transmitted by an optical fiber, according the specification in IEC 60044-8, clause 6.2.2.1, Table 10, column "glass fiber":

Note: BFOC is also know as ST.

SmpCnt

Verify: The attribute "SmpCnt" behaves as specified in IEC 61850-7-2: "The parameter SmpCnt shall contain the values of a counter, which is incremented each time a new sample of the analogue value is taken. The sample values shall be kept in the right order. If the counter is used to indicate time consistency of various sampled values, the counter shall be reset by an external synchronization event."

IEC61850-9-2: SmpCnt will be incremented each time a new sampling value is taken. The counter shall be set to zero if the sampling is synchronised by clock signal (SmpSynch = TRUE) and the synchronising signal occurs. See NOTE 2: When sync pulses are used to synchronise merging units, the counter shall be set to zero with every sync pulse. The value 0 shall be given to the data set where the sampling of the primary current coincides with the sync pulse.

Operating without synchronization: If the merging unit does not receive a synchronization signal and has left the hold-over mode, "SmpSynch" in the SV message shall be set to FALSE. "SmpCnt" shall wrap as if a synchronization pulse would be present.

RefreshTime is optional (PIXIT). The example in Annex A is without RefreshTime!

7.2.4 Calculations to be done in the IED: If neutral current and / or voltage are not measured, the merging unit has to calculate these values as a sum of the phase values. However, since the receiver needs to know, if the values are calculated or measured, the merging unit has to indicate that in the "derived" bit in the respective quality field.

And the ICD file has to indicate that by the ‘virtual’ attribute of the substation section modelling the neutral current CT (PIXIT)

ANNEX A

- Verify format of the SV messages as specified in figure 3: MAC, VLAN tag, APPID

- Verify format of the SV messages as specified in figure 4:

  - MSVCB01: APDU with 1 ASDU

  - MSVCB02: APDU with 8 ASDU

- Verify format of the SV messages as specified in figure 5: dataset PhsMeas1

- Verify sampling rate is 80 and/or 256 samples per cycle for 50Hz

- Verify sampling rate is 80 and/or 256 samples per cycle for 60Hz

- Verify the sampled values match with the analog signals (magnitude accuracy check, 100 A (r.m.s.) = 141'421 * 1mA and 100 V is 14'142 * 10mV (peak) for pure sinusoidal signals. Check for several point on range for (classical secondary) voltages and amps. Full rated primary voltages/amps are out of scope.

- Scaling is done by the IED! PIXIT shall describe how this is done.  For example it could be said that MU does no scaling, since it delivers the values as primary values. Sensor ratings are often implicit or specified by a legacy method since for non-conventional sensors, the classical ratings do not apply. In such cases, the sensor interface is neither accessible nor specified. The "scaling" is part of the signal conditioning. If classical CTs/VTs are used as sensors, the use of the LNs TCTR and TVTR may apply for setting the MU.

ANNEX B: SCL EXAMPLE

No verification

ANNEX C: ACCURACY

In a merging unit kind of device the magnitude accuracy is mainly limited by the accuracy of CT or VT. Measuring the amplitude accuracy of the device (the Analog to Digital conversion) may be out-of-scope for the test. ABB: This would no longer be a conformance test, but a function test.  (see also Annex A). However we like to perform a "plausibility" accuracy test with an accuracy of about 1% on a few points on the range.

Delay

The delay from sampling to sending the sample message shall be less then the maximum delay as specified in 44-8 clause 5.3.2.  In case samples are not synchronised the delay shall be = 2 * Ts or 3 * Ts (Ts being the inverse of the digital data rate). Ts is the time between two messages. For example datarate for 50Hz protection Ts 1/4000msg/sec = 0.25ms. So the rated delay in this case is either 0.5 or 0.75 msec.

If the merging unit is intended to be used with synchronization pulses, the rated delay time is 3 ms (+10 % – 100 %) for all data rates, since it is not relevant for phase error.

Synchronization accuracy (par 7.2.2)

The accuracy of the PPS signal (and possible resulting phase error) is out-of-scope for the device under test.

ANNEX D: DYNAMIC RANGES

No verification

ANNEX E: REFERENCE ARROWS

Verify the reference arrow orientation system for an IED. How? FST: Inject a primary value and make a "polarity check" to verify if the wiring and finally the wiring instructions.  Richard: Wiring is out-of-scope for the conformance test

Abstract test cases

Detailed test procedures

To be defined when abstract test cases are stable.

PIXIT template

- FX connector type = ST or MT-RJ

- support test mode?

- samples with RefreshTime?

- sample rate 80 and/or 256?

- are neutral sampled values calculated?

- support 3 or 4 voltage and/or 3-4 currents signals

- describe how the samples are scaled

- support 50 and/or 60 Hz nominal frequency?

- what is the time synch hold-over period?

- which quality bits are supported?

- max length for IED name?

- what is the (rated) delay time between taking the sample and sending the corresponding SV message?

Revision history

| Version | Changes |
| --- | --- |
| 0.1 | Initial version |
| 0.2 | Comments received via e-mail |
| 0.3 | Comments received during the 3 december teleconference |

# Text boxes

KEMA Nederland B.V.  Utrechtseweg 310, 6812 AR Arnhem  P.O. Box 9035, 6800 ET Arnhem  The Netherlands

T +31 26 3 56 91 11  F +31 26 3 89 24 77  contact@kema.com  www.kema.com  Registered Arnhem 09080262

Copyright © KEMA Nederland B.V., Arnhem, the Netherlands. All rights reserved.

This document  may be distributed to UCA international users group members only.

KEMA Nederland B.V. and/or its associated companies disclaim liability for any direct, indirect, consequential or incidental damages that may result from the use of the information or data, or from the inability to use the information or data.

.