539-MOC/INC 2011-v2.4

Conformance Test Procedures for Server Devices with IEC 61850-8-1 interface Revision 2.4

On request of the UCA International Users Group

July 28,2012

Author Richard Schimmel

KEMA Nederland

| author : Richard Schimmel | 06-11-11 | reviewed : Marijn flohil | 06-16-11 |
| --- | --- | --- | --- |
| B 183 pages 5 annexes | RS | approved : UCAIUG testsub | 08-17-11 |

| Revision | Changed test procedures | New test procedures |
| --- | --- | --- |
| Rev 2.0 02Apr2007 | Released to Users Group |  |
| Rev 2.1 26Sep2007 | Updated according to Charlotte test sub committee meeting: Sg2, Sg3, SgN3, Rp7, Rp9, RpN4, Br7, Br11, Br13, Ctl7, CtlN2, CtlN3, CtlN4, CtlN9, CtlN10, CtlN11, Does2, Does5, SBOes3, SBOes5 | RpN7, BrN7, Tm3, SgN5 |
| Rev 2.2 08Oct2007 | Updated according to Dean Ouellette comments: Glossary, SgN5, Gop8 |  |
| Rev 2.2a 08Jan2009 | Updated test descriptions according to TPCL December 2008 for the following procedures: AssN4, BrN4, BrN6, Cnf6, Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, Dset6, DsetN2, DsetN15, Ft1, FtN1, Gop3, Gop6, RpN6, SBOes2, SBOns1, Sg4, SgN1b, SgN2, SgN3, SgN4, SgN5, Srv6, Sub3, SubN1 |  |
| Rev 2.2b 07Apr2009 | Updated test descriptions according to TPCL March 3, 2009 for the following procedures: CtlN2, FtN1, Srv6 |  |
| Rev 2.3 17Aug2011 | Updated many test cases according to telephone conferences April and May and June 2001. | Rp12, Br14, Gos4 Added PIXIT template Added server certificate template |
| Rev 2.4 07Jul2012 | Updated GOOSE test cases so that GOOSE only devices can be tested. | Created Gop7a, 7b, 9a, 9b, 10a, and 10b. Revised GosN5 and GosN6 |

Remark: the detailed change history is not part of this report but is archived by KEMA.

CONTENTS

page

1	Introduction	7

1.1	Identifications	7

1.2	Background	8

1.3	Purpose of this document	8

1.4	Contents of this document	8

1.5	Glossary	9

2	References	9

2.1	Normative	9

2.2	Other	10

3	The Conformance test	11

3.1	Components in the test environment	11

3.2	Overview of the test suite	12

4	Test results	12

5	Conclusions and recommendations	14

5.1	Recommendations following from the test	14

Annex A – Detailed Test procedures and results	15

A4.1	Application association	23

A4.2	Server & Logical Device & Logical Node & Data	29

A4.3	Data set	41

A4.4	Substitution	58

A4.5	Setting group control	62

A4.6	Unbuffered Reporting	70

A4.7	Buffered Reporting	86

A4.8	Logging [Future]	114

A4.9	Generic Object Oriented Substation Events (GOOSE)	115

A4.10	Control	132

A4.10a	 Control DOns	144

A4.10b	Control SBOns	146

A4.10c	 Control DOes	150

A4.10d	Control SBOes	152

A4.11	Time and time synchronization	158

A4.12	File transfer	161

A4.13	Combinations & free form testing	164

Annex B	 Detailed description of test results	165

Annex C	 TICS template for Server	166

Annex D	 PIXIT template for Server	170

Annex E	 Server Certificate Template	182

# Introduction

## Identifications

The following table gives the exact identification of tested equipment and test environment used for this conformance test.

| DUT | <complete description of the device under test, type, hardware / software version> |
| --- | --- |
| MANUFACTURER | <name, location of the manufacturer of the DUT> |
| PICS | <complete reference description of the PICS> |
| MICS | <complete reference description of the MICS> |
| TICS | <complete reference description of the TICS> |
| PIXIT | <complete reference description of the PIXIT> |
| ICD | <complete reference description of the ICD configuration file> |
| SCD | <complete reference description of the SCD or CID configuration file> |
| TEST INITIATOR | <the initiator of the test, name, address, contact person> |
| TEST FACILITY | <test facility name> <accredited/recognized to issue Level A/B/C Certificates> |
| TEST ENGINEER | <name and e-mail address of test engineer> |
| TEST SESSION | <date and location(s) of the test session> |
| SIMULATOR | <name and type conformance test simulator version X.Y with reference test suite, version X.Y and Test parameters file> |
| ANALYSER | <name and type analyzer, version X.Y> |
| EQUIPMENT SIMULATOR | <name and type equipment simulator> |
| TIME MASTER | <name and type of time master> |

NOTE; the TEST FACILITY or MANUFACTURER can provide the documents in digital or printed format

## Background

<OPTIONAL, short description on the environment where the DUT will be used>

The TEST FACILITY’s assignment was to answer the following question:

“Does the protocol implementation of the DUT, conform to the IEC 61850 standard and the PICS, MICS, PIXIT and ICD specifications as configured with SCD?”

To answer this question, TEST FACILITY has performed a conformance test of the IEC 61850 implementation in the DUT. This test has been performed according procedures and conditions set forth in IEC 61850 part 10 and UCA IUG Quality Assurance Program.

TEST FACILITY is accredited/recognized by the UCA IUG to perform formal UCA conformance tests and issue the Level A/B UCA certificate.

## Purpose of this document

The purpose of this document is to describe the conformance test procedure and results of the TEST SESSION concerning the IEC 61850 implementation in the DUT.

The test results are the basis of the conformance statement.

## Contents of this document

Chapter 2 shows the list of relevant normative and other references, used to provide input for the conformance test.

Chapter 3 describes the various relevant components for the conformance test and their configuration as used in the conformance test, including the DUT. This chapter also gives an overview and introduction to the various test groups that together constitute the conformance test.

Chapter 4 and 5 give an overview and summary of the test results, the conclusion(s) and recommendations.

Annex A specifies the detailed test procedures and their outcome. Annex B contains detailed comments on test results, for instance when a defect is detected, including the actual message flow if appropriate. Annex C provides a template for TICS documents. This template also specifies the mandatory technical issues. Annex D and E provide templates for the PIXIT document and UCA IEC 61850 Server certificate.

## Glossary

DUT		Device Under Test

ICD		IED configuration description in SCL-format

MICS		Model Implementation Conformance Statement

PICS		Protocol Implementation Conformance Statement

TICS		Technical Issues Implementation Conformance Statement

PIXIT		Protocol Implementation eXtra Information for Testing

SCD		Substation configuration description in SCL-format

SCL		Substation Configuration Language

SNTP		Simple Network Time Protocol

TISSUE	Technical issue

TPAA		Two-Party Application Association (Client-Server relationship)

UCAIUG	UCA International Users Group

# References

## Normative

The tests defined in this document are based on the following IEC 61850 documents.

IEC/TR 61850-1, Communication networks and systems in substations – Part 1: Introduction and overview; First edition 2003-04

IEC/TS 61850-2, Communication networks and systems in substations – Part 2: Glossary; First edition 2003-08

IEC 61850-3, Communication networks and systems in substations – Part 3: General requirements; First edition 2003-01.

IEC 61850-4, Communication networks and systems in substations – Part 4: System and project management; First edition 2003-01

IEC 61850-5, Communication networks and systems in substations – Part 5: Communication requirements for functions and device models; First edition 2003-07

IEC 61850-6, Communication networks and systems in substations – Part 6: Substation Automation System configuration language; First edition 2004-03

IEC 61850-7-1, Communication networks and systems in substations – Part 7-1: Basic communication structure for substation and feeder equipment – Principles and models; First edition 2003-07

IEC 61850-7-2, Communication networks and systems in substations – Part 7-2: Basic communication structure for substation and feeder equipment – Abstract communication service interface (ACSI); First edition 2003-05

IEC 61850-7-3, Communication networks and systems in substations – Part 7-3: Basic communication structure for substation and feeder equipment – Common data classes and attributes; First edition 2003-05

IEC 61850-7-4, Communication networks and systems in substations – Part 7-4: Basic communication structure for substation and feeder equipment – Compatible logical node and data object addressing; First edition 2003-05

IEC 61850-8-1, Communication networks and systems in substations – Part 8-1: Specific communication service mapping (SCSM) – Mappings to MMS (ISO/IEC 9506-1 and ISO/IEC 9506-2) and to ISO/IEC 8802-3; First edition 2004-05

IEC 61850-10, Communication networks and systems in substations – Part 10: Conformance testing; First edition 2005-05

## Other

IS 9646 – OSI – Conformance testing methodology and framework

UCA International User Group: Conformance Test Procedures for Server Devices with IEC 61850-8-1 Interface Revision 2.3,  April, 2011

UCA International User Group: Test Procedures Change List (TPCL) for IEC 61850 server test procedures revision 2.3,  Version XX, <date>

UCA International User Group: Quality Assurance Program for IEC Device Implementation Testing and Test System Accreditation and Recognition, Version 2.0, 17 June, 2006

UCA International User Group: Quality Assurance Program Addendum for IEC 61850 Specific Product Testing, Version 1.0,  March 8, 2006

http://tissues.iec61850.com/

# The Conformance test

## Components in the test environment

The test environment consists of the following components:

- DUT

- SIMULATOR

- ANALYSER

- EQUIPMENT SIMULATOR

- Ethernet switching HUB

- SCL engineering tools

- Time master

Figure 3.1 The test environment

## Overview of the test suite

The server test cases are structured as follows:

- Documentation and version control (IEC 61850-4)

- Device performance (IEC 61850-5)

- Configuration file (IEC 61850-6)

- Data model (IEC 61850-7-3 and IEC 61850-7-4)

- Mapping of ACSI models and services (IEC 61850-7-2 and IEC 61850-8-1)

  - Application association

  - Server & Logical Device & Logical Node & Data

  - Data set

  - Substitution

  - Setting group control

  - Reporting

  - Logging

  - Generic Substation events

  - Control

  - Time and time synchronization

  - File transfer

  - Combinations

The PICS is used to select the applicable test procedures to be included in the test.

# Test results

Tables 4.1 and 4.2 in this Chapter give an overview of the conformance test results. References shown in the table columns refer to the individual test procedures in Annex A. The Mandatory column indicates the mandatory test cases and the Conditional column indicates the same for the conditional test cases. The Inconclusive column indicates those test cases that did not pass nor fail.

Table 4.1	Overview of applicable test cases passed for DUT

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | Ass1, Ass2, Ass3, AssN2, AssN3, AssN4, AssN5 Srv1, Srv2, Srv3, Srv4, Srv5, SrvN1abcd, SrvN4 | AssN6 Srv6, Srv7, Srv8, Srv9, Srv10, SrvN1e, SrvN1f, SrvN2, SrvN3 |
| 2: Data Sets | Dset1, Dset10a, DsetN1ae | Dset10b, DsetN1b, DsetN16 |
| 2+: Data Set Definition | Dset2, Dset3, Dset4, Dset5, Dset6, Dset7, Dset8, Dset9 DsetN1cd, DsetN2, DsetN3, DsetN4, DsetN5, DsetN6, DsetN7, DsetN8, DsetN9, DsetN10, DsetN11, DsetN12, DsetN13, DsetN14, DsetN15 |  |
| 3: Substitution | Sub1, Sub2, Sub3, SubN1 |  |
| 4: Setting Group Selection | Sg1, SgN1a | Sg3 |
| 4+: Setting Group Definition | Sg2, Sg4, SgN1b, SgN2, SgN3, SgN4, SgN5 |  |
| 5: Unbuffered Reporting | Rp1, Rp2, Rp3, Rp4, Rp7, Rp10, Rp12 RpN1, RpN2, RpN3, RpN4 | Rp5, Rp6, Rp8, Rp9, Rp11, RpN5, RpN6, RpN7 |
| 6: Buffered Reporting | Br1, Br2, Br3, Br4, Br7, Br8, Br9, Br12, Br14 BrN1, BrN2, BrN3, BrN4, BrN5 | Br5, Br6, Br10, Br11, Br13, BrN6, BrN7 |
| 6+: Enhanced buffered reporting | BrE1, BrE2, BrE3, BrE6, BrE7, BrE8, BrE9, BrE10, BrE11 | BrE4, BrE5, BrE12 |
| 9a: GOOSE publish | Gop2, Gop3, Gop4, Gop7a,Gop9a,Gop10a | Gop1, Gop5, Gop6, Gop7b, Gop8, Gop9b, Gop10b GopN1, GopN2a, GopN2b |
| 9b: GOOSE subscribe | Gos1a, Gos2, Gos3, GosN1, GosN2, GosN3, GosN4, GosN5, GosN6 | Gos1b, Gos4 |
| 12a: Direct control | CtlN3, CtlN8 DOns1, DOns3 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 DOns2, DOns4, DOns5 |
| 12b: SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, SBOns2 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 SBOns3, SBOns4, SBOns5 |
| 12c: Enhanced Direct Control | CtlN3, CtlN8 DOes2, DOes5 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11, DOes1, DOes3, DOes4 |
| 12d: Enhanced SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, CtlN9 SBOes1, SBOes2, SBOes3 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11, SBOes4, SBOes5, SBOes6, SBOes7 |
| 13: Time sync | Tm1, Tm2, TmN1 | Tm3, TmN2 |
| 14: File transfer | Ft1, Ft2ab, Ft4, FtN1ab | Ft2c, Ft3, FtN1c |

Table 4.2	Overview of applicable test cases failed, inconclusive or comments for DUT

| Conformance Block | Inconclusive | Failed | Comment |
| --- | --- | --- | --- |
| <block> | <testcase> | <testcase> | <testcase> |

# Conclusions and recommendations

Based on the test results described in this report, TEST FACILITY declares the tested IEC 61850 implementation in the DUT has shown/not shown to be non-conforming to IEC 61850-6, 7-1, 7-2, 7-3, 7-4 and 8-1 as specified in the PICS, MICS, PIXIT, TICS and ICD and configured according to the SCD.

## Recommendations following from the test

The following comments and recommendations apply for the DUT:

<Comments and Recommendations from TEST FACILITY>

# Annex A – Detailed Test procedures and results

- Documentation (IEC 61850-4)

| Id | Test procedure | Verdict |
| --- | --- | --- |
| Doc1 | Check if the manufacturer documentation and hardware / software versions of the DUT do match: PICS MICS PIXIT TICS Hardware/software versions match | ( Passed ( Failed ( Inconclusive |
| Doc2 | Verify the MICS describes the semantics of all non-standard Logical Nodes, Data Objects, Data Attributes and enumerations | ( Passed ( Failed ( Inconclusive |

- Configuration file (IEC 61850-6)

| Id | Test procedure | Verdict |
| --- | --- | --- |
| Cnf1 | Test if the ICD configuration file conforms to the SCL schema (IEC 61850-6) | ( Passed ( Failed ( Inconclusive |
| Cnf2 | Check if the ICD configuration file corresponds with the actual data names, data types, data-sets, pre-defined data values exposed by the DUT on the network. When more data or services are exposed, attach a list and set the test result to Passed. When less data or services are exposed the test result is Failed. | ( Passed ( Failed ( Inconclusive |
| Cnf3 | Change at least 5 end-user configurable parameters that are exposed by the DUT on the network in the SCD configuration file, configure the DUT using the SCD configuration file (using the supplied configuration tool) and check the updated configuration using online services corresponds with the updated SCD file. Restore the original SCD file and re-configure the DUT to its original state. Check that the configuration is changed back. | ( Passed ( Failed ( Inconclusive |
| Cnf4 | Check if the server capabilities in the ICD “services” section do match with the IED capabilities | ( Passed ( Failed ( Inconclusive |
| Cnf5 | In case the control model is fixed (not configurable) check if the ICD correctly initializes the ctlModel values for all controllable objects | ( Passed ( Failed ( Inconclusive |

- Data model (IEC 61850-7-3 and IEC 61850-7-4)

| Id | Test procedure | Verdict |
| --- | --- | --- |
|  | Verify presence of mandatory objects for each LN Passed when all objects/attributes are present, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Verify presence of conditional presence true objects for each LN Passed when all objects/attributes are present, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Verify non-presence of conditional presence false objects. Passed when these objects/attributes are not present, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Verify data model mapping according to applicable SCSM concerning name length and object expansion Passed when mapping is according to applicable SCSM, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Verify data model mapping according to applicable SCSM concerning organisation of functional components Passed when mapping is according to applicable SCSM, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Verify data model mapping according to applicable SCSM concerning naming of control blocks and logs Passed when mapping is according to applicable SCSM, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Verify data type of all objects for each LN. Passed when data type of all objects/attributes do match with the IEC 61850-7-3, IEC 61850-7-4 and the applicable SCSM, when failed attach a list Data types should also match the Approved technical issues: IEC 61850-7-2 Tissue #35, #37, #38, #39, #40, #42 IEC 61850-7-3 Tissue #58 IEC 61850-7-4 Tissue #72, #75, #76 IEC 61850-8-1 Tissue #114, #120 | ( Passed ( Failed ( Inconclusive |
|  | Verify data attribute values from the device are in specified range (this is a continuous effort during the whole conformance test) Passed when all values are in range, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Check if manufacturer specific data model extensions are implemented according to the extension rules in IEC 61850-7-4 Annex A. (only when extension are implemented) Passed when all extensions are implemented according to the rules, when failed attach a list | ( Passed ( Failed ( Inconclusive |
|  | Check if the order of the data attributes within the Data Object types match with IEC 61850-7-3 Passed when all attributes are in matching order | ( Passed ( Failed ( Inconclusive |
|  | Check if the order of the data objects within the Logical Node types match with IEC 61850-7-4 Passed when all objects are in matching order | ( Passed ( Failed ( Inconclusive |

Note: the attached list(s) should indicate the complete object reference, data type/common data class/data attribute type, M/O/Condition presence indication (from IEC 61850-7-3 and IEC 61850-7-4), attribute value and applicable error indication.

- Mapping of ACSI models and services (IEC 61850-7-2 and applicable SCSM)

- Application association

- Server & Logical Device & Logical Node & Data

- Data set

- Substitution

- Setting group control

- Unbuffered Reporting

- Buffered Reporting

- Logging [FUTURE]

- Generic object oriented substation events (GOOSE)

- Control

- Time and time synchronization

- File transfer

- Combinations & Free testing

The following table specifies which ACSI services are mandatory/optional for each conformance block.

Table A.4.1: ACSI services per conformance block

| Conformance Block | Mandatory | Optional |
| --- | --- | --- |
| 1: Basic Exchange | Associate, Abort, Release GetServerDirectory GetLogicalDeviceDirectory GetLogicalNodeDirectory (DATA) GetDataValues GetDataDirectory, GetDataDefinition | GetAllDataValues SetDataValues |
| 2: Data Set | GetLogicalNodeDirectory (DATA-SET) GetDataSetValues GetDataSetDirectory | SetDataSetValues |
| 2+: Data Set Definition | CreateDataSet DeleteDataSet |  |
| 3: Substitution | SetDataValues GetDataValues |  |
| 4: Setting Group Selection | SelectActiveSG GetSGCBValues | GetSGValues |
| 4+: Setting Group Definition | SelectEditSG GetSGValues SetSGValues ConfirmEditSGValues |  |
| 5: Unbuffered Reporting | Report GetURCBValues SetURCBValues |  |
| 6: Buffered Reporting | Report GetBRCBValues SetBRCBValues |  |
| 6+: Enhanced buffered reporting | When tissue #453 is implemented |  |
| 7: Logging | GetLCBValues GetLogicalNodeDirectory (LOG) QueryLogByTime or QueryLogAfter GetLogStatusValues | SetLCBValues |
| 9a: GOOSE publish | SendGOOSEMessage (publish) | GetGoCBValues SetGoCBValues |
| 9b: GOOSE subscribe | SendGOOSEMessage (subscribe) |  |
| 9c: GOOSE mngt | GetGoReference GetGOOSEElementNumber |  |
| 10: Sampled values part 9-1 pub/sub | <no ACSI service associated> |  |
| 11: Sampled values part 9-2 pub/sub | SendUSVMessage or SendMSVMessage | GetxSVCBValues SetxSVCBValues |
| 12a: Direct control | Operate | TimeActivatedOperate |
| 12b: SBO control | Select, Cancel, Operate | TimeActivatedOperate |
| 12c: Enhanced Direct Control | Operate CommandTermination | TimeActivatedOperate |
| 12d: Enhanced SBO control | SelectWithValue, Cancel, Operate CommandTermination | TimeActivatedOperate |
| 13: Time sync | TimeSynchronization |  |
| 14: File transfer | GetFile GetFileAttributeValues | SetFile DeleteFile |

The following table specifies which test procedures are mandatory/conditional for each conformance block (defined in Quality Assurance Plan, QAP). Conditions refer to the SCL: IED - Services section, the PICS or PIXIT.

Table A.4.2: Test procedures per conformance block

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | Ass1, Ass2, Ass3, AssN2, AssN3, AssN4, AssN5 Srv1, Srv2, Srv3, Srv4, Srv5, SrvN1abcd, SrvN4 | AssN6 Semantics: Srv9, Srv10 PICS-AlternateAccess: Srv8, SrvN1f PICS-SetDataValues: Srv6, Srv7, SrvN1e, SrvN2, SrvN3 |
| 2: Data Sets | Dset1, Dset10a, DsetN1ae | SCL-SetDataSetValues: Dset10b, DsetN1b, DsetN16 |
| 2+: Data Set Definition (SCL-DynDataSet) | Dset2, Dset3, Dset4, Dset5, Dset6, Dset7, Dset8, Dset9 DsetN1cd, DsetN2, DsetN3, DsetN4, DsetN5, DsetN6, DsetN7, DsetN8, DsetN9, DsetN10, DsetN11, DsetN12, DsetN13, DsetN14, DsetN15 |  |
| 3: Substitution | Sub1, Sub2, Sub3, SubN1 |  |
| 4: Setting Group Selection (SCL-ConfSG) | Sg1, SgN1a | PICS-GetSGValues: Sg3 |
| 4+: Setting Group Definition (SCL-SGEdit) | Sg2, Sg4, SgN1b, SgN2, SgN3, SgN4, SgN5 |  |
| 5: Unbuffered Reporting | Rp1, Rp2, Rp3, Rp4, Rp7, Rp10,Rp12, RpN1, RpN2, RpN3, RpN4 | PICS-Segmentation: Rp5 SCL-RCB.DatSet=dyn: Rp6 PIXIT-URCB visible to all clients: RpN5 PIXIT-Unsupported options: RpN6 PIXIT-data objects: Rp8 PIXIT-data attributes: Rp9 Controllable mode: Rp11 Assign: RpN7 |
| 6: Buffered Reporting | Br1, Br2, Br3, Br4, Br7, Br8, Br9, Br12. Br14, BrN1, BrN2, BrN3, BrN4, BrN5 | PICS-Segmentation: Br5 SCL-RCB.DatSet=dyn: Br6 PIXIT-Unsupported options: BrN6 PIXIT-data objects: Br10 PIXIT-data attributes: Br11 Controllable mode: Br13 Assign: BrN7 |
| 6+: Enhanced buffered reporting (when tissue #453 is implemented) | BrE1, BrE2, BrE3, BrE6, BrE7, BrE8, BrE9, BrE10, BrE11 | ResvTms: BrE4, BrE5 SCL-RCB.DatSet=dyn: BrE12 |
| 7: Logging | To be defined |  |
| 9a: GOOSE publish | Gop2, Gop3, Gop4, Gop7a, Gop9a, Gop10a | PICS-GetGoCBValues: Gop1, Gop7b PIXIT-Test mode: Gop5 PIXIT – SCD file used to configure: Gop7a PICS-SetGoCBValues: Gop6, Gop8, Gop9a, Gop9b, GopN1 Dataset to large: GopN2a, GopN2b PIXIT-FCD data objects: Gop10b |
| 9b: GOOSE subscribe | Gos1a, Gos2, Gos3, GosN1, GosN2, GosN3, GosN4, GosN5, GosN6 | No VLAN: Gos1b Support FCD: Gos4 |
| 9c: GOOSE mngt (SCL-GSEDir) | Gom1, GomN1 |  |
| 12a Direct control | CtlN3, CtlN8 DOns1, DOns3 | PIXIT-Test mode: Ctl2 PIXIT-Check: Ctl7 PICS-TimeActivatedOperate: Ctl4, DOns2, DOns4, DOns5 PIXIT-Mode: CtlN10 Local: CtlN11 |
| 12b SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4 SBOns2 | PIXIT-Test mode: Ctl2 PIXIT-Check: Ctl7 PICS-TimeActivatedOperate: Ctl4, SBOns3, SBOns5 PIXIT-Operate-Many: SBOns4, SBOns5 PIXIT-Mode: CtlN10 Local: CtlN11 |
| 12c Enhanced Direct Control | CtlN3, CtlN8 DOes2, DOes5 | PIXIT-Test mode: Ctl2 PIXIT-Check: Ctl7 PICS-TimeActivatedOperate: Ctl4, DOes1, DOes3, DOes4 AddCauses: CtlN6 PIXIT-Mode: CtlN10 Local: CtlN11 |
| 12d Enhanced SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, CtlN9 SBOes1, SBOes2, SBOes3 | PIXIT-Test mode: Ctl2 PIXIT-Check: Ctl7 PICS-TimeActivatedOperate: Ctl4, SBOes4, SBOes5, SBOes7 PIXIT-Operate-Many: SBOes6 AddCauses: CtlN6 PIXIT-Mode: CtlN10 Local: CtlN11 |
| 13 Time sync | Tm1, Tm2, TmN1 | PIXIT-ClockFailure: TmN2 PIXIT-Time zone: Tm3 |
| 14 File transfer | Ft1, Ft2ab, Ft4, FtN1ab | PICS-SetFile: Ft3 PICS-DeleteFile: Ft2c, FtN1c |

Note that AssN1, Ctl5, Ctl6, CtlN5, CtlN7, SBOns1 are not applicable for IEC 61850 part 8-1 and not referenced in this table.

The following paragraphs describe the abstract test cases and corresponding detailed test procedures. New test cases should be added at the end of the table. The revision history shows the history of new/changed test procedures.

## A4.1	Application association

Abstract test cases

|  | Associate and release a TPAA association (IEC 61850-7-2 clause 7.4) |
| --- | --- |
|  | Associate and client-abort TPAA association (IEC 61850-7-2 clause 7.4) |
|  | Associate with maximum number of clients simultaneously (PIXIT) |

|  | Check that with incorrect authentication parameters and authentication turned on at server the association fails, and with authentication turned off the server associates (IEC 61850-7-2 clause 7.4) |
| --- | --- |
|  | Check that with incorrect association parameters at server or client the association fails (IEC 61850-7-2 clause 7.4, PIXIT) |
|  | Set up maximum+1 associations, verify the last associate is refused |
|  | Disconnect the communication interface, the DUT should detect link lost within a specified period |
|  | Interrupt and restore the power supply, the DUT should accept an association request when ready |
|  | Re-use of dropped association resource |

Detailed test procedures

| Ass1 | Associate and release a TPAA association | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4 IEC 61850-8-1 clause 10.2 |
| Expected result 2. DUT sends Associate response+ 3. DUT sends Release response+ |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client request Associate 3. Client request Release 4. Repeat step 2 and 3 250 times |
| Comment |
| Ass2 | Associate and client-abort TPAA association | ( Passed ( Failed ( Inconclusive |
| IEC 61850-7-2 clause 7.4 IEC 61850-8-1 clause 10.2 |
| Expected result 2. DUT sends Associate response+ 3. DUT sends Abort response+ |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client requests Associate 3. Client requests Abort 4. Repeat step 2 and 3 250 times |
| Comment |

| Ass3 | Associate with maximum number of clients simultaneously | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4, IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 2. DUT sends Associate response+ for each client 3. DUT sends Release response+ for each client |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client 1 to max requests Associate 3. Client 1 to max requests Release 4. Repeat step 2 and 3 250 times |
| Comment |

| AssN2 | Associate with incorrect association parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4 IEC 61850-8-1 clause 10.2, PIXIT |
| Expected result 1. Client sends Associate response+ 2. Client sends Release response+ 4. DUT sends Associate response- when PIXIT indicates the DUT verifies the parameter, otherwise the DUT sends Associate response+ |
| Test description 1. Configure the SIMULATOR and DUT with correct association and authentication parameters and request Associate 2. Client requests Release 3. Configure the SIMULATOR and DUT with correct authentication parameters and one of the following incorrect configurable association parameters: called / calling transport selector called / calling session selector called / calling presentation selector called / calling AP title called / calling AE qualifier 4. Client requests Associate 5. When DUT sends Associate response+, Client sends Release request 6. Repeat step 1 to 5 for the next association parameter |
| Comment The following table indicates the associate response results with incorrect: called / calling transport selector - / + called / calling session selector - / + called / calling presentation selector - / + called / calling AP title + / + called / calling AE qualifier + / + “-“ = associate failed, DUT sends response- “+” = associate succeeded, DUT sends response+ |

| AssN3 | Associate with maximum+1 number of clients simultaneously | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4, IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 2. DUT sends Association response+ for a count of at least the maximum server associate value in the PIXIT 3. DUT sends Release response+ |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client sends Associate request until DUT sends response- 3. Client sends release for all accepted associations 4. Repeat step 2 and 3 250 times |
| Comment |

| AssN4 | Detection of lost link | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4, IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 2. DUT sends Associate response+ 3. DUT sends GetDataValues response+ 6. DUT sends no response |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client requests Associate 3. Client requests a correct GetDataValues 4. Disconnect the physical link, between two Ethernet switches (preventing Ethernet hardware error detection at both client and server), some seconds longer than the KEEP ALIVE timeout specified in the PIXIT 5. Connect the physical link 6. Verify the DUT has lost the association by sending a correct GetDataValues request |
| Comment |

| AssN5 | Power supply interrupt | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4, IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 2. DUT sends Associate response+ 4. The DUT sends Associate response+ |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client requests Associate 3. Interrupt and restore the DUT power supply until the DUT is initialised 4. Client requests Associate and DUT response+ |
| Comment |

| AssN6 | Re-use of dropped association resource | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 7.4, IEC 61850-8-1 clause 10.2 PIXIT |
| Expected result 2. DUT sends at least one Associate response+ 3. DUT sends Abort response+ 5. DUT sends Associate response+ 6. DUT sends GetDataValues response+ 7. Note: DUT should internally abort all stack layers, a half-open TCP connection is not allowed 9. DUT sends Associate response+. 10. DUT sends GetDataValues response+ |
| Test description 1. Configure the SIMULATOR and DUT with the correct association and authentication parameters 2. Client 1 requests associations until they are refused 3. Client 1 aborts the last association 4. DUT issues keepalives on all associations 5. Client 2 requests association and sends keepalives 6. Client 2 requests a correct GetDataValues 7. Disconnect physical link between Client 2 and the switch, some seconds longer than the KEEPALIVE timeout specified in the PIXIT 8. Connect the physical link to Client2 9. Client 2 requests association 10. Client 2 requests a correct GetDataValues |
| Comment |

## A4.2	Server & Logical Device & Logical Node & Data

Abstract test cases

|  | Request GetServerDirectory(LOGICAL-DEVICE) and check response (IEC 61850-7-2 clause 6.2.2) |
| --- | --- |
|  | For each GetServerDirectory(LOGICAL-DEVICE) response issue a GetLogicalDeviceDirectory request and check response (IEC 61850-7-2 clause 8.2.1) |
|  | For each GetLogicalDeviceDirectory response issue a GetLogicalNodeDirectory(DATA) request and check response (IEC 61850-7-2 clause 9.2.2) |
|  | For each GetLogicalNodeDirectory(DATA) response issue a GetDataDirectory request and check response (IEC 61850-7-2 clause 10.4.4) GetDataDefinition request and check response (IEC 61850-7-2 clause 10.4.5) GetDataValues request and check response (IEC 61850-7-2 clause 10.4.2) |
|  | Issue one GetDataValues request with the maximum number of data values and check response |
|  | For each write enabled DATA object issue a SetDataValues request and check response (IEC 61850-7-2 clause 10.4.2) |
|  | Issue one SetDataValues request with the maximum number of data values and check response |
|  | Request GetAllDataValues for each functional constraint and check response (IEC 61850-7-2 clause 9.2.3) |
|  | Evaluate the semantic of selected (volt/amp) analogue measurements: Verify analogue value (plausibility check, not accuracy) Verify quality bits, force situations to set specific quality bits Verify (UTC) timestamp value and quality (plausibility check, not accuracy) Verify scaling, range and units, change a setting and verify resulting value Verify dead band, change dead band and verify result Verify limit indications |
|  | Evaluate the semantic of selected status points: Verify status value Verify quality bits, force situations to set specific quality bits Verify (UTC) timestamp value and quality (plausibility check, not accuracy) |

|  | Request following data services with wrong parameters (unknown object, name case mismatch, wrong logical device or wrong logical node) and verify response- service error GetServerDirectory(LOGICAL-DEVICE) (IEC 61850-7-2 clause 6.2.2) GetLogicalDeviceDirectory (IEC 61850-7-2 clause 8.2.1) GetLogicalNodeDirectory(DATA) (IEC 61850-7-2 clause 9.2.2) GetAllDataValues (IEC 61850-7-2 clause 9.2.3) GetDataValues (IEC 61850-7-2 clause 10.4.2) SetDataValues (IEC 61850-7-2 clause 10.4.3) GetDataDirectory (IEC 61850-7-2 clause 10.4.4) GetDataDefinition (IEC 61850-7-2 clause 10.4.5) |
| --- | --- |
|  | Request SetDataValues of ENUMERATED data with out-of-range value and verify response- service error (IEC 61850-7-2 clause 10.4.2) |
|  | Request SetDataValues with mismatching data type (e.g. int-float) and verify response- service error (IEC 61850-7-2 clause 10.4.2) |
|  | Request SetDataValues for read-only data values and verify response- service error (IEC 61850-7-2 clause 10.4.2) |

Detailed test procedures

| Srv1 | GetServerDirectory(LOGICAL-DEVICE) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 6.2.2 IEC 61850-8-1 clause 9.3 |
| Expected result 1. DUT sends Association response+ 2. DUT sends GetServerDirectory(LOGICAL-DEVICE) response+ with a list of logical devices |
| Test description 1. Client requests correct Association 2. Client requests GetServerDirectory(LOGICAL-DEVICE) 3. Continue with Srv2 |
| Comment |

| Srv2 | GetLogicalDeviceDirectory | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 8.2.1 IEC 61850-8-1 clause 11.1 |
| Expected result 1. DUT sends GetLogicalDeviceDirectory response+ with a list of logical nodes |
| Test description 1. For each responded logical device Client requests GetLogicalDeviceDirectory 2. Continue with Srv3 |
| Comment |

| Srv3 | GetLogicalNodeDirectory(DATA) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 IEC 61850-8-1 clause 12.3.1 |
| Expected result 1. DUT sends GetLogicalNodeDirectory(DATA) response+ with a list of data |
| Test description 1. For each responded logical node directory Client requests GetLogicalNodeDirectory(DATA) 2. Continue with Srv4 |
| Comment Note: IEC 61850-8-1 maps both GetLogicalNodeDirectory(DATA) and GetLogicalDeviceDirectory to GetNameList service. |

| Srv4 | GetDataDirectory, GetDataDefinition and GetDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.4, 10.4.5 and 10.4.2 IEC 61850-8-1 clause 13.2.3, 13.2.4 and 13.2.1 |
| Expected result 1. DUT sends GetDataDirectory response+ 2. DUT sends GetDataDefinition response+ 3. DUT sends GetDataValues response+ |
| Test description For each responded data object Client requests a: 1. GetDataDirectory 2. GetDataDefinition 3. GetDataValues |
| Comment Note1: IEC 61850-8-1 maps the functional constraint between the Logical Node and Data Object. As such Srv4 issues requests including the functional constraint: <LD>/<LN><FC><DO> Note2: IEC 61850-8-1 maps both GetDataDirectory and GetDataDefinition to GetVariableAccessAttributes |

| Srv5 | GetDataValues with multiple data and data hierarchy | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.2 IEC 61850-8-1 clause 13.2.1 |
| Expected result 1. DUT sends GetDataValues response+ with equal number of data values DUT sends GetDataValues response+ with requested data hierarchy Note: It is allowed that the GetDataValues on logical node level may fail for large logical nodes caused by server MMS PDU size limitations. |
| Test description 1. Client requests one GetDataValues with multiple data objects 2. Client requests one GetDataValues of at least the following data objects for the supported data hierarchy level: Functional constrained data: LLN0$ST$Mod Functional constrained data attribute: LLN0$ST$Mod$stVal Functional constrained data attribute type attribute |
| Comment |

| Srv6 | SetDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.2 PIXIT |
| Expected result 1. DUT sends SetDataValues response- 2. DUT sends SetDataValues response- for read-only data and response+ for write enabled data (as specified in the standard, ICD or PIXIT) 3. and 5. DUT sends SetDataValues response+ 4. and 6. DUT sends GetDataValues response+ with requested value, the value does match |
| Test description For each data object with functional constraint ST, MX, EX 1. Client sends a SetDataValues with the current value For each data object with functional constraint CF, SP, DC 2. Client sends a SetDataValues with the current value For the first write-enabled data object (if any) 3. Client sends a SetDataValues with a valid new value 4. Client sends a GetDataValues request and check the value does match 5. Client sends a SetDataValues with the original value 6. Client sends a GetDataValues request and check the value does match |
| Comment |

| Srv7 | SetDataValues with multiple data objects | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.2 |
| Expected result 1. DUT sends GetDataValues response+ with original values 2. DUT sends SetDataValues response+ 3. DUT sends GetDataValues response+ with the new values |
| Test description 1. Client requests one GetDataValues with multiple data objects 2. Client requests one SetDataValues with multiple data objects with new valid values 3. Client request one GetDataValues |
| Comment Tested with … objects |

| Srv8 | GetAllDataValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.3 IEC 61850-8-1 clause 12.3.2 |
| Expected result 1. DUT sends GetAllDataValues response+ 2. DUT sends GetAllDataValues response+ |
| Test description For each Logical Node and supported functional constraint the Client sends a GetAllDataValues request using MMS Alternate Access where the alternate access contains at least an allowed Data FC: ST, MX, CF, SP, DC, EX. For each Logical node the Client sends a GetAllDataValues request using object reference <IED><LD>/<LN>$<FC> where FC can be: ST, MX, CF, SP, DC, EX. |
| Comment |

| Srv9 | Semantic of measured value (MV) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-3 clause 6.2, 6.3, 6.4, 6.5, 7.4.2, PIXIT |
| Expected result 1 to 4: The timestamp accuracy should match with the PICS time stamp accuracy The time stamp value should match the actual time (plausibility check) Default quality attribute value should be supplied when the functionality of the related quality attribute is not supported (PIXIT) When supported the scaling, range, units and dead band functionality should be supplied. |
| Test description 1. Force EQUIPMENT SIMULATOR to change the measured value, Client request GetDataValues and checks the instantaneous / dead banded value does match the forced change 2. Force situations to set specific quality bits, Client request GetDataValues and checks the quality does match the forced situation validity: good, invalid, questionable detail: overflow, out of range, bad reference, oscillatory, failure, old data, inaccurate, inconsistent source: process or substituted test operator blocked 3. Change the scale, range and units and repeat step 1 4. Change the dead band and repeat step 1 and verify differences in the instantaneous and dead banded value |
| Comment PIXIT indicates the following quality bits are supported: <to be completed> The following quality bits could be forced for the specified data object: <to be completed> Scaling, range, units and dead band are supported <to be adjusted>. |

| Srv10 | Semantic of single and double point status (SPS, DPS) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-3 clause 6.2, 7.3.2 and 7.3.3 PIXIT |
| Expected result 1. DUT sends GetDataValues Response+, values matches the forced changes 2. The timestamp accuracy should match with the PICS time stamp accuracy. Default quality attribute value should be supplied when the functionality of the related quality attribute is not supported (PIXIT) |
| Test description 1. Force EQUIPMENT SIMULATOR to change a single and double point status value, Client request GetDataValues and checks the value does match the forced change 2. Force situations to set specific quality bits, Client request GetDataValues and checks the quality does match the forced situation validity: good, invalid, questionable detail: bad reference, oscillatory, failure, old data, inaccurate, inconsistent source: process or substituted test operator blocked 3. For 1 and 2 verify the time stamp value and time stamp accuracy (PICS) |
| Comment PIXIT indicates the following quality bits are supported: <to be completed> The following quality bits could be forced for the specified data object: <to be completed> |

| SrvN1 | LD/LN/Data services with incorrect parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 6.2.2, 8.2.1, 9.2-3, 10.4.2-5 IEC 61850-8-1 clause 9.3, 12.3.1-2, 13.2.1-4, Table 27, Table 23 Tissue #116 |
| Expected result DUT sends MMS service error with error class access object-non existent (table 27) DUT sends MMS service error with error class access object-non existent (table 27) DUT sends MMS service error with error class access object-non existent (table 27) DUT sends response with Access result “object-non-existent” (table 23) DUT sends response with Access result “object-non-existent” (table 23) DUT sends response with Access result “object-non-existent” (table 23) |
| Test description Client requests the following data services with wrong parameters (unknown object, logical device and/or logical node, known object but with a name case mismatch when applicable): GetLogicalDeviceDirectory GetLogicalNodeDirectory (for part 8-1 same as a)) GetDataDirectory / GetDataDefinition (same for part 8-1) GetDataValues SetDataValues GetAllDataValues |
| Comment |

| SrvN2 | SetDataValues with out-of-range ENUMERATED value | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.1-4 |
| Expected result 1. DUT sends response with data access error “object-value-invalid” (see note below table 23) |
| Test description 1. Client sends a SetDataValues request of an ENUMERATED data object with an out-of-range value |
| Comment |

| SrvN3 | SetDataValues with mismatching data type | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.1-4, Table 23 |
| Expected result 1 to 4: DUT sends response with data access error “type-inconsistent” |
| Test description 1. Client sends a SetDataValues request with an integer data object with a float value 2. Client sends a SetDataValues request with a float data object with an integer value 3. Client sends a SetDataValues request with a boolean data object with a float value 4. Client sends a SetDataValues request with a bitstring data object with a float value |
| Comment |

| SrvN4 | SetDataValues of read-only data objects | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 10.4.3 IEC 61850-8-1 clause 13.2.1-4, Table 23 |
| Expected result 1. DUT sends response with data access error “object-access-denied” |
| Test description 1. Client sends a SetDataValues request with an read-only data object |
| Comment Compare Srv6 |

## A4.3	Data set

Abstract test cases

| Dset1 | Request GetLogicalNodeDirectory(DATA-SET) and check response (IEC 61850-7-2 clause 9.2.2) For each response issue a GetDataSetValues request and check response (IEC 61850-7-2 clause 11.3.2) GetDataSetDirectory request and check response (IEC 61850-7-2 clause 11.3.6) |
| --- | --- |
| Dset2 | Request a persistent CreateDataSet with one member and with maximum possible members and check response (IEC 61850-7-2 clause 11.3.4) and verify that the persistent data set is visible for another client |
| Dset3 | Request a non-persistent CreateDataSet with one, maximum members and check response (IEC 61850-7-2 clause 11.3.4) and verify that the persistent data set is not visible for another client |
| Dset4 | Create and delete a persistent dataset, create the dataset again with the same name with one extra data value / re-ordered member and check the members |
| Dset5 | Create and delete a non-persistent dataset, create the dataset again with the same name with one extra data value / re-ordered member and check the members |
| Dset6 | Create a non-persistent dataset, release/abort the association, associate again and check the dataset has been deleted (IEC 61850-7-2 clause 11.1) |
| Dset7 | Create a persistent dataset, release/abort the association, associate again and check the dataset is still present (IEC 61850-7-2 clause 11.1) |
| Dset8 | Create and delete a persistent data set several times and verify every data set can be created normally |
| Dset9 | Create and delete a non-persistent data set several times and verify every data set can be created normally |
| Dset10 | Verify SetDataSetValues / GetDataSetValues with GetDataValues and SetDataValues |

| DsetN1 | Request following data set services with wrong parameters (unknown object, name case mismatch, wrong logical device or wrong logical node) and verify response- service error : GetDataSetValues (IEC 61850-7-2 clause 11.3.2) SetDataSetValues (IEC 61850-7-2 clause 11.3.3) CreateDataSet (IEC 61850-7-2 clause 11.3.4) DeleteDataSet (IEC 61850-7-2 clause 11.3.5) GetDataSetDirectory (IEC 61850-7-2 clause 11.3.6) |
| --- | --- |
| DsetN2 | Create a persistent dataset with the same name twice, and verify response- service error |
| DsetN3 | Create a non-persistent dataset with the same name twice, and verify response- service error |
| DsetN4 | Create more than maximum number of persistent data sets and verify response- service error |
| DsetN5 | Create more than maximum number of non-persistent datasets and verify response- service error |
| DsetN6 | Create a persistent dataset with more than maximum number of members and verify response- service error |
| DsetN7 | Create a non-persistent dataset with more than maximum number of members and verify response- service error |
| DsetN8 | Create a persistent dataset with unknown member verify response- service error |
| DsetN9 | Create a non-persistent dataset with unknown member verify response- service error |
| DsetN10 | Create a persistent dataset with no member, and verify response- service error |
| DsetN11 | Create a non-persistent dataset with no member, and verify response- service error |
| DsetN12 | Delete a (pre-defined) non-deletable dataset, and verify response- service error |
| DsetN13 | Delete a persistent dataset twice, and verify response- service error |
| DsetN14 | Delete a non-persistent dataset twice, and verify response- service error |
| DsetN15 | Delete a dataset referenced by a (report) control class, and verify response- service error (IEC 61850-7-2 clause 11.1) |
| DsetN16 | Request SetDataSetValues with a dataset with one or more read-only members, and verify response- service error |

Detailed test procedures

| Dset1 | GetLogicalNodeDirectory, GetDataSetDirectory, GetDataSetValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.3.2, 11.3.6 IEC 61850-8-1 clause 14.3 |
| Expected result 1. DUT sends a GetLogicalNodeDirectory (DATA-SET) response+ 2. DUT sends a GetDataSetDirectory response+ 3. DUT sends a GetDataSetValues response+ |
| Test description 1. For each logical node Client requests a GetLogicalNodeDirectory (DATA-SET) 2. For each returned data set, Client requests a GetDataSetDirectory 3. For each returned data set, Client requests a GetDataSetValues |
| Comment |

| Dset2 | Persistent data set, one and max no. of members and accessibility | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.4 IEC 61850-8-1 clause 12.3.1, 14.3.3, PICS, PIXIT |
| Expected result 1. DUT sends CreateDataSet response+ 2. DUT responds GetLogicalNodeDirectory(DATA-SET) response+. The response includes the data set name to Client2 3. See result 1 and 2 |
| Test description 1. Client1 requests a persistent CreateDataSet with one member 2. Client2 requests GetLogicalNodeDirectory(DATA-SET) 3. Repeat step 1 and 2 but now with the maximum number of members |
| Comment |

| Dset3 | Non-persistent data set, one and max no. of members and accessibility | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.4 IEC 61850-8-1 clause 12.3.1, 14.3.3 PIXIT |
| Expected result 1. DUT sends CreateDataSet response+ 2. DUT sends GetLogicalNodeDirectory(DATA-SET) response+, but does not list the created data set in the response 3. See result 1 and 2 |
| Test description 1. Repeat Dset2 but now for a non-persistent data set |
| Comment |

| Dset4 | Create and delete persistent data set with same name, one extra member, and re-ordered members | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.4, 11.3.5, 11.3.6 IEC 61850-8-1 clause 12.3.1, 14.3.3, 14.3.4, 14.3.5 |
| Expected result 1. DUT sends a CreateDataSet response+ 2. DUT sends: - GetLogicalNodeDirectory(DATA-SET) response+, the data set is present. - DUT sends GetDataSetDirectory response+ and contains the members as defined 3. DUT sends a DeleteDataSet response+ 4. DUT sends: - CreateDataSet response+ - GetLogicalNodeDirectory(DATA-SET) response+, the data set is present - GetDataSetDirectory response+ and contains the members as defined members as defined. The extra member is available 5. DUT sends a DeleteDataSet response+ 6. DUT sends: - CreateDataSet response+ - GetLogicalNodeDirectory(DATA-SET) response+, the data set is present - GetDataSetDirectory response+ and contains the members in the order as defined |
| Test description 1. Client requests a persistent CreateDataSet with a number of members (at least two) 2. For this just created data set, Client requests a GetLogicalNodeDirectory(DATA-SET) and a GetDataSetDirectory 3. Client requests a DeleteDataSet on the just created data set 4. Client requests again a persistent CreateDataSet but now with one extra member. Clients requests a GetLogicalNodeDirectory(DATA-SET) and a GetDataSetDirectory 5. Client requests a DeleteDataSet on the just created data set 6. Client requests again a persistent CreateDataSet with the same members as step 2 but with the first two members reordered (the first member is now listed as the second member, the second member is now listed as the first member). Request a GetLogicalNodeDirectory(DATA-SET) and a GetDataSetDirectory |
| Comment |

| Dset5 | Create and delete non-persistent data set with same name , one extra member, and re-ordered members | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.4, 11.3.5, 11.3.6 IEC 61850-8-1 clause 12.3.1, 14.3.3, 14.3.4, 14.3.5 |
| Expected result 1. See Dset4 |
| Test description 1. Repeat Dset4 but now with a non-persistent data set |
| Comment |

| Dset6 | Deletion of non-persistent dataset after Release | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.2, 11.3.4, 11.3.5 IEC 61850-8-1 clause 12.3.1, 14.3.1, 14.3.3, 14.3.4 |
| Expected result 1. DUT sends a response+ 2. DUT sends a response+ 3. The data set is not available, it is deleted. DUT sends MMS service error with error class access object-non-existent (table 23) 4. See result 1, 2 and 3 |
| Test description 1. Client requests a non-persistent CreateDataSet with at least one member 2. Client requests Release and then Associate 3. Client requests a GetDataSetValues for the just created data set 4. Repeat step 1, 2 and 3 but in 2 use Abort instead of Release |
| Comment |

| Dset7 | Non-deletion of persistent dataset after Release | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.2,11.3.4, 11.3.5 IEC 61850-8-1 clause 12.3.1, 14.3.1, 14.3.3, 14.3.4 |
| Expected result 1. DUT sends a response+ 2. DUT sends a response+ 3. DUT sends a response+. The data set is available, it is not deleted 4. See result 1, 2 and 3 |
| Test description 1. Repeat Dset6 but now for a persistent data set |
| Comment |

| Dset8 | Create and delete persistent data set several times | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4, 11.3.5 IEC 61850-8-1 clause 14.3.3, 14.3.4 |
| Expected result 1. DUT responds with a CreateDataSet response+ 2. DUT responds with a DeleteDataSet response+ 3. Every data set can be created and deleted without problems |
| Test description 1. Client requests a persistent CreateDataSet with a number of members (at least two) 2. Client requests a DeleteDataSet on the just created data set 3. Repeat step 1 and 2 250 times |
| Comment |

| Dset9 | Create and delete non-persistent data set several times | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4, 11.3.5 IEC 61850-8-1 clause 12.3.1, 14.3.3, 14.3.4 |
| Expected result 1. See Dset8 |
| Test description 1. Repeat Dset8 but now for a non-persistent data set |
| Comment |

| Dset10 | GetDataSetValues, SetDataSetValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 11.1, 11.3.2,11.3.4, 11.3.5 IEC 61850-8-1 clause 12.3.1, 14.3.1, 14.3.3, 14.3.4 |
| Expected result a) The DUT returns the corresponding values for GetDataSetValues and GetDataValues b) Before the SetDataSetValues: The values returned by GetDataSetValues and GetDataValues correspond After the SetDataSetValues: The values returned by GetDataSetValues and GetDataValues correspond and contain the new values as set with SetDataSetValues and SetDataValues. Every service request results in a corresponding response+ |
| Test description a) Select or create a data set with read-only elements Client requests a GetDataSetValues Client requests a GetDataValues for each member of the dataset. b) Select or create a data set with writable elements Client requests a GetDataSetValues Client requests a GetDataValues for each member of the dataset. Client requests a SetDataSetValues with different values than received by GetDataValues Client requests a GetDataSetValues Client requests a SetDataValues for each member of the dataset. Client request GetDataSetValues |
| Comment |

| DsetN1 | DataSet services with illegal parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.2, 11.3.3, 11.3.4, 11.3.5, 11.3.6 IEC 61850-8-1 clause 14.3.1, 14.3.2, 14.3.3, 14.3.4, 14.3.5, Tissue #165, #377 |
| Expected result a) DUT sends ServiceError with errorClass access “object-non-existent” (Tissue #165) b) DUT sends ServiceError with errorClass access “object-non-existent” (Tissue #165) c) DUT sends ServiceError with errorClass definition “invalid-address” (table 31) d) DUT sends DeleteDataSet with numberMatched 0, numberDeleted 0 (Tissue #377) e) DUT sends ServiceError with errorClass definition “object-undefined” (table 35) |
| Test description Test a) 1. Client requests a GetDataSetValues with an unknown data set name as DataSetReference. 2. Client requests a GetDataSetValues for a known data set but with the first character of the DataSetReference in opposite case. E.g. if the first character is 'M', use 'm' now. If it was 'm', use 'M' 3. Client requests a GetDataSetValues with a non-existing Logical Device in the DataSetReference 4. Client requests a GetDataSetValues where the Logical Device in the DataSetReference is replaced by another, existing Logical Device in this DUT, but which does not contain a dataset with the same name 5. Client requests a GetDataSetValues with a non-existing Logical Node in the DataSetReference 6. Client requests a GetDataSetValues where the Logical Node in the DataSetReference is replaced by another, existing Logical Node in another Logical Device in the DUT Test b) Repeat step 1 to 6 for SetDataSetValues Test c) Repeat step 1 to 6 for CreateDataSet Test d) Repeat step 1 to 6 for DeleteDataSet Test e) Repeat step 1 to 6 for GetDataSetDirectory |
| Comment 4. Only if DUT contains more than one Logical Device 6. Only if DUT contains more than one Logical Device |

| DsetN2 | Create a persistent dataset twice | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 |
| Expected result 1. DUT sends a response+, 2. DUT sends MMS service error with error class definition object-exists (table 31) |
| Test description 1. Client requests a CreateDataSet for a persistent data set with at least one member 2. Client requests the same CreateDataSet again |
| Comment |

| DsetN3 | Create a non-persistent dataset twice | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 |
| Expected result See DsetN2 |
| Test description 1. Repeat DsetN2 but now for a non-persistent data set |
| Comment |

| DsetN4 | Create more than max no. of data sets, persistent | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3, PICS, PIXIT |
| Expected result 1. The DUT responds with a CreateDataSet response+ for every created data set 2. The DUT responds with a CreateDataSet response- |
| Test description 1. Client requests as many persistent CreateDataSet’s as supported by the DUT 2. Client requests one more CreateDataSet |
| Comment |

| DsetN5 | Create more than max no. of data sets, non-persistent | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT |
| Expected result 1. See DsetN4 |
| Test description 1. Repeat DsetN4 with non-persistent datasets |
| Comment |

| DsetN6 | Create persistent data set with more than max. no of data members | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT |
| Expected result 1. The DUT responds with a CreateDataSet response- |
| Test description 1. Client requests a persistent CreateDataSet with the maximum number + 1 of data members as supported by the DUT |
| Comment |

| DsetN7 | Create non-persistent data set with more than max. no of data members | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 PIXIT |
| Expected result 1. See DsetN6 |
| Test description 1. Repeat DsetN6 with non-persistent datasets |
| Comment |

| DsetN8 | Create persistent data set with unknown data reference | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3 |
| Expected result 1. The DUT responds with a CreateDataSet response- |
| Test description 1. Client requests a persistent CreateDataSet with at least two data references of which one is unknown |
| Comment |

| DsetN9 | Create non-persistent data set with unknown data reference | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3, PICS |
| Expected result 1. See DsetN8 |
| Test description 1. Repeat DsetN8 but now for a non-persistent data set |
| Comment |

| DsetN10 | Create persistent data set without data references | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3, PICS |
| Expected result 1. The DUT responds with a CreateDataSet response- |
| Test description 1. Client requests a persistent CreateDataSet without data references |
| Comment |

| DsetN11 | Create non-persistent data set without data references | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4 IEC 61850-8-1 clause 14.3.3, PICS |
| Expected result 1. See DsetN10 |
| Test description 1. Repeat DsetN10 but now for a non-persistent data set |
| Comment |

| DsetN12 | Delete a pre-configured data set | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.5 IEC 61850-8-1 clause 14.3.4, PICS, MICS, PIXIT |
| Expected result 1. The DUT sends a DeleteDataSet response+ with Number deleted = 0 |
| Test description 1. Client requests a DeleteDataSet to delete a pre-configured, non-deletable data set, not referenced in a report control block |
| Comment |

| DsetN13 | Delete a persistent data set twice | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4, 11.3.5 IEC 61850-8-1 clause 14.3.3, 14.3.4, PICS |
| Expected result 1. DUT sends a CreateDataSet response+ DUT sends a response+ with Number deleted = 1 DUT sends a response+ with Number deleted = 0 |
| Test description 1. Client requests a persistent CreateDataSet Client requests a DeleteDataSet for the created data set in step 1 Client requests the same DeleteDataSet |
| Comment |

| DsetN14 | Delete a non-persistent data set twice | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4, 11.3.5 IEC 61850-8-1 clause 14.3.3, 14.3.4, PICS |
| Expected result See DsetN13 |
| Test description 1. Repeat DsetN13 but now for a non-persistent data set |
| Comment |

| DsetN15 | Delete referenced data set | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.1, 11.3.4, 11.3.5, 14.2 IEC 61850-8-1 clause 14.3.3, 14.3.4, 17.2, PICS |
| Expected result 1. DUT sends a CreateDataSet response+ 3. DUT sends a DeleteDataSet response+ with Number deleted = 0 4. DUT sends a DeleteDataSet response+ with Number deleted = 0 |
| Test description 1. Client requests a persistent CreateDataSet. 2. Client configures and enables a (buffered or unbuffered) RCB with this data set 3. Client requests a DeleteDataSet on the data set created in step 1 4. Client disables the RCB and requests a DeleteDataSet on the data set created in step 1 5. Repeat step 1 to 4 for non-persistent dataset and unbuffered RCB |
| Comment |

| DsetN16 | SetDataSetValues on read-only data attribute | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 11.3.2, 11.3.4 IEC 61850-8-1 clause 14.3.1, 14.3.3, PICS, PIXIT |
| Expected result 1. DUT sends a CreateDataSet response+ 2. DUT sends a SetDataSetValues response- |
| Test description 1. Client requests a persistent CreateDataSet where one or more of the members of the data set is a read-only data attribute 2. Client requests a SetDataSetValues with data set created in step1 |
| Comment |

## A4.4	Substitution

Abstract test cases

|  | Disable subEna and set subVal, subMag, subCMag, subQ and verify the substituted values are not transmitted when subEna is disabled and are transmitted when subEna enabled (IEC 61850-7-2 clause 12) |
| --- | --- |
|  | Verify that in case the association fails, the substituted values shall remain unchanged |
|  | Verify transmission of substituted values after reboot |

|  | Verify setting subVal, subMag, subCMag, subQ and subID when subEna is already enabled (clause 12) |
| --- | --- |

Detailed test procedures

| Sub1 | Transmission of substituted values | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 |
| Expected result 1. DUT sends GetDataValues response+ with process values DUT sends SetDataValues response+ DUT sends SetDataValues response+ DUT sends GetDataValues response+ with substituted values DUT sends SetDataValues response+ DUT sends GetDataValues response+ with process values |
| Test description Client requests GetDataValues of ST/MX data value Client requests SetDataValues of the SV data value attributes Client requests SetDataValues to enable substitution Client requests GetDataValues of ST/MX data value Client requests SetDataValues to disable substitution Client requests GetDataValues of ST/MX data value |
| Comment |

| Sub2 | Transmission of substituted values on failed association | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 |
| Expected result DUT sends GetDataValues response+ with process values DUT sends SetDataValues response+ DUT sends SetDataValues response+ DUT aborts association DUT sends Associate response+ DUT sends GetDataValues response+ with substituted values DUT sends SetDataValues response+ |
| Test description Client requests GetDataValues of ST/MX data value Client requests SetDataValues of the SV data value attributes Client requests SetDataValues to enable substitution Client requests Abort Client requests Associate Client requests GetDataValues of ST/MX data value Client requests SetDataValues to disable substitution |
| Comment |

| Sub3 | Transmission of substituted values after reboot | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 PIXIT |
| Expected result DUT sends GetDataValues response+ with process values DUT sends SetDataValues response+ DUT sends SetDataValues response+ DUT reboots DUT sends Associate response+ DUT sends GetDataValues response+ with substituted values when substituted values are Non-Volatile and with process values when Volatile (PIXIT) DUT sends SetDataValues response+ |
| Test description Client requests GetDataValues of ST/MX data value Client requests SetDataValues of the SV data value attributes Client requests SetDataValues to enable substitution Test engineer reboots DUT Client requests Associate Client requests GetDataValues of ST/MX data value Client requests SetDataValues to disable substitution |
| Comment In 7-2 the behaviour after reboot is not specified. PIXIT may describe cases where a local automatic function disables substitution |

| SubN1 | Substitute values when substitution is already enabled | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 12 IEC 61850-8-1 clause 15 |
| Expected result DUT sends GetDataValues response+ with process values DUT sends SetDataValues response+ DUT sends SetDataValues response+ DUT sends GetDataValues response+ with substituted values DUT sends SetDataValues response+ DUT sends GetDataValues response+ with new substituted values DUT sends SetDataValues response+ DUT sends GetDataValues response+ with process values |
| Test description Client requests GetDataValues of a ST and/or MX data object Client requests SetDataValues of the SV data value attributes Client requests SetDataValues to enable substitution Client requests GetDataValues of a ST and/or MX data object Client requests SetDataValues of the SV with new data value attributes Client requests GetDataValues of the ST and/or MX data object Client requests SetDataValues to disable substitution Client requests GetDataValues of the ST and/or MX data object |
| Comment |

## A4.5	Setting group control

Abstract test cases

|  | Request GetLogicalNodeDirectory(SGCB) and check response+ |
| --- | --- |
|  | Verify the following setting group state machine path (IEC 61850-7-2 clause 13 figure 18); SelectEditSG Use SetSGValues [FC=SE] to change values Use GetSGValues [FC=SE] to verify the new values ConfirmEditSGValues |
|  | Verify SelectActiveSG (IEC 61850-7-2 clause 13 figure 18); SelectActiveSG of the first setting group GetSGCBValues to verify active setting group Use GetSGValues [FC=SG] to verify the values are of first setting group Repeat for all setting groups |
|  | Verify that after loss of association the client can use SelectEditSG again to copy the values to the edit buffer (IEC 61850 7-2 clause 13.3.3.1) |

| SgN1a | Request following setting group selection services with wrong parameters (out of range values, or non existent/null setting group) and verify response- service error SelectActiveSG (IEC 61850-7-2 clause 13.3.2) GetSGValues [FC=SG] (IEC 61850-7-2 clause 13.3.6) GetSGCBValues (IEC 61850-7-2 clause 13.3.7) |
| --- | --- |
| SgN1b | Request following setting group definition services with wrong parameters (out of range values, or non existent/null setting group) and verify response- service error SelectEditSG (IEC 61850-7-2 clause 13.3.3) SetSGValues (IEC 61850-7-2 clause 13.3.4) ConfirmEditSGValues (IEC 61850-7-2 clause 13.3.5) GetSGValues [FC=SE] (IEC 61850-7-2 clause 13.3.6) |
| SgN2 | Request SetSGValues (FC=SG), verify response- service error |
| SgN3 | Request SetSGValues (FC=SE) when EditSG = 0, verify response- service error |
| SgN4 | Request SelectEditSG of the first setting group, change one value and SelectEditSG of the second setting group without (ConfirmEditSGValues). Verify the changes will be lost |
| SgN5 | Verify that the values of the active setting group can be edited and confirmed |

Detailed test procedures

| Sg1 | GetLogicalNodeDirectory(SGCB) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2, 13.3.7 IEC 61850-8-1 clause 12.3.1, 16.2.6 |
| Expected result 1. DUT sends GetLogicalNodeDirectory(SGCB) response+ with a list of SGCB’s 2. DUT sends GetSGCBValues response+ |
| Test description 1. For each logical node Client requests GetLogicalNodeDirectory(SGCB) 2. For each SGCB Client requests GetSGCBValues() |
| Comment |

| Sg2 | SelectEditSG, SetSGValues, ConfirmEditSGValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2 |
| Expected result 1. DUT sends SelectEditSG response+ 2. DUT sends SetSGValues [FC=SE] response+ 3. DUT sends GetSGValues [FC=SE] response+ 4. DUT sends ConfirmEditSGValues response+, the value of CnfEdit shall return to FALSE once the storage is completed. |
| Test description Client requests SelectEditSG Client requests SetSGValues [FC=SE] to change all values in the group Client requests GetSGValues [FC=SE] to verify the new values Client requests ConfirmEditSGValues |
| Comment Note: Sg3 must be executed after Sg2 to verify changed values are active |

| Sg3 | SelectActiveSG and GetSGValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2.1, 16.2.5 PIXIT |
| Expected result DUT sends SelectActiveSG response+ DUT has set the activated setting group value DUT sends GetSGValues response+ |
| Test description Client requests SelectActiveSG of the first setting group Client requests GetSGCBValues Client requests GetSGValues [FC=SG] to verify the values in the first setting group repeat step 1 and 2 for other setting groups for this SGCB |
| Comment |

| Sg4 | SelectEditSG after lost association | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.3.3.1 IEC 61850-8-1 clause 16.2.2 PIXIT |
| Expected result DUT sends SelectEditSG response+ DUT sends SetSGValues [FC=SE] response+ DUT aborts the association DUT send associate response+ DUT sends SelectEditSG response+ and the values in the edit buffer are refreshed. DUT sends SetSGValues [FC=SE] response+ DUT sends ConfirmEditSGValues response+ |
| Test description Client requests SelectEditSG of the first setting group Client requests SetSGValues [FC=SE] to change values Clients aborts the association Client requests associate Client requests SelectEditSG of the first setting group Client requests SetSGValues [FC=SE] to change values Client requests ConfirmEditSGValues |
| Comment |

| SgN1a | Setting group selection services with wrong parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2 PIXIT |
| Expected result DUT sends SelectActiveSG response- DUT sends GetSGValues response- DUT sends GetSGCBValues response- |
| Test description Client requests SelectActiveSG with null / out-of-range setting group Client requests GetSGValues with FC=SG unknown object Client requests GetSGCBValues with unknown object |
| Comment |

| SgN1b | Setting group definition services with wrong parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2 PIXIT |
| Expected result DUT sends SelectEditSG response- DUT sends SetSGValues response- with applicable service error DUT sends ConfirmEditSGValues response- DUT sends GetSGValues response- |
| Test description Client requests SelectEditSG with out-of-range setting group Client requests SetSGValues with unknown object / wrong data type Client requests ConfirmEditSGValues with unknown object Client requests GetSGValues with FC=SE unknown object |
| Comment |

| SgN2 | SetSGValues [FC=SG] | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2.3 |
| Expected result DUT sends SetSGValues response- |
| Test description Client requests a valid SetSGValues [FC=SG] |
| Comment |

| SgN3 | SetSGValues when EditSG=0 | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2.3 |
| Expected result 2. DUT sends SetSGValues response- |
| Test description 1. Client requests SelectEditSG with edit setting group 0 2. Client requests a valid SetSGValues [FC=SE] |
| Comment |

| SgN4 | SelectEditSG without confirmation | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2.2, 16.2.3, 16.2.5 |
| Expected result DUT sends SelectEditSG response+ DUT sends GetSGValues [FC=SE] response+ DUT sends SetSGValues [FC=SE] response+ DUT sends GetSGValues [FC=SE] response+ DUT sends SelectEditSG response+ DUT sends GetSGValues [FC=SE] response+, note that changes are lost |
| Test description Client requests SelectEditSG of the first setting group Client requests GetSGValues [FC=SE] to read the original values Client requests SetSGValues [FC=SE] to change all values in the group Client requests GetSGValues [FC=SE] to verify the new values Client requests SelectEditSG of the first setting group again Client requests GetSGValues [FC=SE] to verify the original values |
| Comment |

| SgN5 | Edit the active setting group | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 13.2, 13.3 IEC 61850-8-1 clause 16.2.1, 16.2.5 |
| Expected result DUT sends SelectActiveSG response+ DUT sends SelectEditSG response+ DUT sends SetSGValues response+ DUT sends ConfirmEditSGValues response+ and the values in the active buffer are refreshed |
| Test description Client requests SelectActiveSG of the first setting group Client requests SelectEditSG of the first setting group Client requests SetSGValues [FC=SE] Client requests ConfirmEditSGValues |
| Comment |

## A4.6	Unbuffered Reporting

Abstract test cases

|  | Request GetLogicalNodeDirectory(URCB) and check response Request GetURCBValues of all responded URCB’s |
| --- | --- |
|  | Verify the reporting of optional fields of a URCB Configure/enable a URCB with all optional fields combinations: sequence-number, report-time-stamp, reason-for-inclusion, data-set-name, and/or data-reference (IEC 61850-7-2 clause 14.2.3.2.2.1), force/trigger a report and check the reports contain the enabled optional fields (7-1 clause 14.2.1) |
|  | Verify the trigger conditions of a URCB Configure and enable a URCB with optional fields: sequence-number, report-time-stamp, reason-for-inclusion, data-set-name, data-reference, buffer-overflow, and entryID and check the reports are transmitted according to the following (supported) trigger conditions: on integrity on update (dupd) on update with integrity on data change (dchg) on data and quality change on data and quality change with integrity period Verify the validity of the ReasonCode (IEC 61850-7-2 clause 14.2.3.2.2.9) Verify that when more trigger conditions are met preferably only one report is generated (IEC 61850-7-2 clause 14.2.3.2.3.2) Verify that reports are only sent when RptEna is set to True. (IEC 61850-7-2 clause 14.2.2.5), when reporting is disabled no reports should be transmitted |
|  | General interrogation Setting the GI attribute of an URCB shall start the general-interrogation process. One report with the current data values will be sent. After initiation of the general-interrogation, the GI attribute is reset to False. (IEC 61850-7-2 clause 14.2.2.13) |
|  | Segmentation of reports Verify that if a long report does not fit in one message, the report is split into sub-reports. Enable sequence-number and report-time-stamp optional field and check validity of: (IEC 61850-7-2 clause 14.2.3.2.2.5) SeqNum (not changed) SubSeqNum (0 for first report, incrementing, roll-over) MoreSeqmentsFollow TimeOfEntry (not changed as SeqNum is not altered) (IEC 61850-7-2 clause 14.2.3.2.2.9) Verify that an update of a data value during sending of a segmented report caused by an integrity or general-interrogation trigger can be interrupted by a report with change of one of the data values with a new sequence number. (IEC 61850-7-2 clause 14.2.3.2.3.5) A new request for general-interrogation shall stop the sending of remaining segments of the GI-report that is still going on. A new GI-report shall start with a new sequence number and the sub-sequence number shall be 0 (IEC 61850-7-2 clause 14.2.3.2.3.4) |
|  | Configuration revision (IEC 61850-7-2 clause 14.2.2.7) Verify that ConfRev represents a count of the number of times the configuration of the data set referenced by DatSet has been changed. Changes that are counted are: deletion of a member of the data-set re-ordering of members in the data-set ConfRev should never be 0 (zero). Verify that after a restart of the server, the value of ConfRev remains unchanged (IEC 61850-7-2 clause 14.2.2.7) Verify that configuration changes data sets due to processing of services are not allowed, changes to be taken into account for the ConfRev are those made by local means like system configuration (IEC 61850-7-2 clause 14.2.2.7. note 1) |
|  | Buffer Time (IEC 61850-7-2 clause 14.2.2.9) Verify that in the case where a second internal notification of the same member of a DATA-SET has occurred prior to the expiration of BufTm, the server: (IEC 61850-7-2 clause 14.2.2.9) shall for status information behave as if BufTm has expired and immediately send the report, restart the timer with value BufTm and process the second notification or may for analogue information behave as if BufTm has expired and immediately transmit the report for transmission, restart the timer with value BufTm and process the second notification or may for analogue information substitute the current value in the pending report with the new one. Configure Buffer Time to 1000 milliseconds and force a data value change of multiple dataset members within buffer time. Server should send not more than one report per buffer time with all the data values changes since last report. Verify that the value 0 for buffer time indicates that the buffer time attribute is not used. (IEC 61850-7-2 clause 14.2.2.9) Verify that the BufTm value can contain at least the value 3600000 (= one hour in milliseconds) |
|  | Verify the DUT can send reports with data objects |
|  | Verify the DUT can send reports with data attributes |
|  | Verify the DUT send any buffered events before the integrity and GI report |
|  | Verify that when the LLN0 Behaviour value changes from On to Off or Blocked no reports should be transmitted anymore for this logical device (IEC 61850-7-4 page 80) |

|  | Request GetURCBValues with wrong parameters and verify response- service error (IEC 61850-7-2 clause 14.2.5.3) |
| --- | --- |
|  | Configure reporting but omit setting one of the trigger options (dchg, qchg, dupd, integrity). When enabled only one report is transmitted (the GI). No reports should be send when generating events (IEC 61850-7-2 clause 14.2.3.2.2.9) |
|  | Setting the integrity period to 0 with TrgOps = integrity will result in no integrity reports will be sent (IEC 61850-7-2 clause 14.2.2.12) |
|  | Incorrect configuration of a URCB: configure when enabled, configure ConfRev and SqNum and configure with unknown data set |
|  | Exclusive use of URCB and lost association Configure a URCB and set the Resv attribute and enable it. Verify another client can not set any attribute of that URCB (IEC 61850-7-2 clause 14.2.4.5) |
|  | Configure unsupported URCB options (PIXIT); Configure unsupported trigger conditions, optional fields and related parameters |
|  | Verify another client can not configure a pre-assigned URCB |

Detailed test procedures

| Rp1 | GetLogicalNodeDirectory(URCB) and GetURCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 and 14.2.5.3 IEC 61850-8-1 clause 12.3.1 and 17.2.4 |
| Expected result 1. DUT sends GetLogicalNodeDirectory(URCB) response+ with a list of URCB’s 2. DUT sends GetURCBValues response+ |
| Test description 1. For each logical node Client requests GetLogicalNodeDirectory(URCB) 2. For each URCB Client requests GetURCBValues() |
| Comment |

| Rp2 | Reporting of optional fields for a URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.8 IEC 61850-8-1 clause 17.1.1.1, 17.2.1, PIXIT |
| Expected result 1. DUT sends SetURCBValues response+ for supported optional fields and response- when one of the optional fields isn’t supported 2. DUT sends SetURCBValues response+ 3. DUT sends a correct report according to trigger condition and IEC 61850-8-1 table 40 with all data set members for reason integrity and otherwise only the changed members. The configured and reported optional fields should match the sequence number is incremented and starts with 0 the report time stamp is in UTC format and matches the trigger time the reason for inclusion matches the trigger condition the configured and reported data set name do match the data-reference(s) match the data set member(s) Configuration revision matches the URCB configuration When segmentation is set the report includes sub sequence number and more segments follow 4. DUT sends SetURCBValues response+ and sends no reports anymore |
| Test description 1. Client configures an available URCB using SetURCBValues with all combinations of the following (supported) optional fields: sequence-number, report-time-stamp, reason-for-inclusion, data-set-name, data-reference and conf-rev 2. Client enables the URCB (set RptEna to True) 3. Client waits for a report (trigger condition integrity) or EQUIPMENT SIMULATOR triggers a report (trigger condition data change) 4. Client disables the URCB (set RptEna to False) 5. Repeat step 1 to 4 for next combination of optional field |
| Comment PIXIT specifies the following optional fields are supported: <to be completed> |

| Rp3 | Trigger conditions for a URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.11 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1, PIXIT |
| Expected result 1. DUT sends SetURCBValues response+ for supported trigger conditions and response- when one of the trigger conditions isn’t supported 2. DUT sends SetURCBValues response+ 3. DUT sends a report according to trigger condition integrity reports should be transmitted immediately at timeout data change reports are transmitted immediately when BufTm=0 data change reports are transmitted after BufTm of first data change when BufTm>0 4. The configured and reported optional fields should match 6. DUT does not sends reports |
| Test description 1. Configure an available RCB using SetURCBValues with all supported optional fields and one of the following (supported) trigger conditions: on integrity [on update (dupd)] [on update with integrity] on data and quality change on data and quality change with integrity period 2. Client enables the RCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces several data changes of one or more data set members in the data set within/outside BufTm 4. Verify the reports are only transmitted according to trigger condition 5. Client disables the RCB, set RptEna to False 6. EQUIPMENT SIMULATOR forces several data changes of one or more data set members in the data set within/outside BufTm 7. Repeat step 1 to 6 for next trigger condition combination |
| Comment PIXIT specifies the following trigger conditions are supported: integrity data/quality change |

| Rp4 | General interrogation URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.13 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1 |
| Expected result 3. DUT sends SetURCBValues() response+ and then sends GI report 4. DUT sends GetURCBValues() response+ with GI attribute not set |
| Test description 1. Client configures an available URCB 2. Client enables the URCB 3. Client requests SetURCBValues() to set the GI report 4. Client requests GetURCBValues() 5. Client disables the URCB |
| Comment |

| Rp5 | Segmentation of reports URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.5 and 14.2.3.2.2.9 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1, PIXIT |
| Expected result 3. The segmented report messages have same SqNum, Incremented SubSeqNum starting with 0 and more segments follow is set and same report timestamp |
| Test description 1. Create or use a pre-configured data set which reported values do not fit in one MMS PDU (reduce the MMS PDU size when necessary) 2. Client configures an available URCB with the data set, with at least the optional fields sequence-number and report timestamp 3. Client enables the RCB and verify the segmentation of integrity reports 4. Client disables the RCB |
| Comment |

| Rp6 | Configuration revision URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.7 IEC 61850-8-1 clause 17.2.1 |
| Expected result 2. DUT sends GetURCBValues() response+ with ConfRev >0 4. The value of ConfRev is incremented |
| Test description 1. Client configures an URCB with a data-set Client request GetURCBValues() Client configures the same URCB with another data-set Client request GetURCBValues() |
| Comment Test procedure is mandatory when datSet of RCB is dynamic see ICD. |

| Rp7 | Buffer time URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.9 IEC 61850-8-1 clause 17.2.1, PIXIT |
| Expected result 3. On second data change in BufTm DUT sends the report of the first data change, and restarts the timer, at BufTm expiration DUT sends the report of the second data change On second data change in BufTm DUT sends the report of the first data change, restarts the timer and at BufTm expiration DUT sends the report of the second data change OR DUT substitutes the current value in the pending report with the new one and sends it at BufTm expiration. Verify the behaviour matches PIXIT DUT sends one report with both status events after BufTm expires DUT sends one report with both analogue events after BufTm expires 7. Each data change result in a report 8. DUT accepts BufTm value 3.600.000 |
| Test description 1. Client configures an available URCB using SetURCBValues with a valid BufTm and all supported optional fields with the trigger conditions: data change and quality change 2. Client enables the URCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces two data changes of the same status data set element in the data set before expiration of BufTm 4. EQUIPMENT SIMULATOR forces two data changes of the same analogue data set element in the data set before expiration of BufTm 5. EQUIPMENT SIMULATOR forces one data change of two different status data set elements in the data set before expiration of BufTm 6. EQUIPMENT SIMULATOR forces one data change of two different analogue data set elements in the data set before expiration of BufTm 7. Client disables the URCB, sets BufTm to zero; repeat step 2, 3 and 4 8. Client disables the URCB, sets BufTm to 3.600.000 9. Client disables the URCB |
| Comment |

| Rp8 | Report data objects (FCD) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.2 |
| Expected result 2. Verify the DUT does report the whole data object |
| Test description 1. Configure DUT to report on data change of one or more data objects 2. Change the data portion of one data object |
| Comment |

| Rp9 | Report data attributes (FCDA) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.2 PIXIT |
| Expected result 2. DUT reports the “data” attribute. Verify that the “timestamp” and “quality” attribute are not sent 3. All attributes are reported 4. All attributes are reported |
| Test description 1. Configure DUT to report a change on one or more data attributes including the “data” attribute and “quality” attribute of the same data object. If the PIXIT indicates timestamps are supported as data set attributes, then configure the “timestamp” attribute for this object 2. Force a change of the data attribute value 3. Request a general interrogation 4. Wait for integrity report |
| Comment |

| Rp10 | Send buffered events before integrity report | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.3 IEC 61850-8-1 clause 17.2 |
| Expected result 3. DUT does send 2 reports: first a report with the buffered data change event and then the integrity report |
| Test description 1. Client configures an available URCB using SetURCBValues with a valid BufTm, a valid IntgPd whose value is smaller than the BufTm value and all supported optional fields with the trigger conditions: data change and integrity 2. Client enables the URCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces a data change in the data set 4. Client disables the URCB |
| Comment |

| Rp11 | Behaviour Off or Blocked stops reporting | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.3 IEC 61850-7-4 page 80 IEC 61850-8-1 clause 17.2 |
| Expected result 2. DUT sends reports 3. DUT should not report the process value change within the logical device 4. DUT sends reports DUT should not report the process value change within the logical device DUT sends reports |
| Test description Client configures an available URCB with trigger condition “dchg” Client enables the URCB, and force a process value data change Client send Operate with LLN0 Mode = Off, and force a process value data change Client send Operate with LLN0 Mode = On, and force a process value data change Client send Operate with LLN0 Mode = Blocked, and force a process value data change Client send Operate with LLN0 Mode = On, and force a process value data change Client disables the URCB |
| Comment |

| Rp12 | Send buffered events before GI | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.3 IEC 61850-8-1 clause 17.2 |
| Expected result 3. DUT does send 2 reports: first a report with the buffered data change event and then the general interrogation report |
| Test description 1. Client configures an available URCB using SetURCBValues with a valid BufTm and all supported optional fields with the trigger conditions: data change and general-interrogation 2. Client enables the URCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces a change in the data set and then the Client requests SetURCBValues (GI=TRUE) before expiration of BufTm 4. Client disables the URCB |
| Comment |

| RpN1 | Incorrect GetURCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.5.3 IEC 61850-8-1 clause 17.1.1.2 |
| Expected result 1. See SrvN1 |
| Test description 1. Repeat SrvN1 for a GetURCBValues |
| Comment |

| RpN2 | No trigger condition URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.2 |
| Expected result 1. DUT does not send reports when reporting is enabled and events are generated |
| Test description 1. Repeat Rp3 with no trigger condition |
| Comment |

| RpN3 | Integrity period zero URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.2 |
| Expected result 3. DUT does not send reports when reporting is enabled |
| Test description 1. Configure an available URCB using SetURCBValues with trigger condition Integrity and integrity period 0 2. Client enables the URCB, set RptEna to True 3. Wait one minute 4. Client disables the URCB, set RptEna to False |
| Comment |

| RpN4 | Incorrect configuration of URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.1.1.2, Table 23 |
| Expected result 2. DUT sends SetURCBValues() response with data access error “temporarily-unavailable” 4. DUT sends SetURCBValues() response with data access error “object-access-denied” 5. DUT sends SetURCBValues() response with data access error “object-value-invalid” |
| Test description 1. Client configures and enables an available URCB 2. Client requests SetURCBValues() with one of the following “dyn” attributes RptID, DatSet, OptFlds, BufTm, TrgOps, IntgPd 3. Client disables the URCB 4. Client requests SetURCBValues() with one of the following attributes ConfRev, SqNum and DatSet (when “fix” or “conf”) 5. Client requests SetURCBValues() with unknown DatSet (when DatSet is “dyn”) |
| Comment |

| RpN5 | Exclusive use of URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1 IEC 61850-8-1 clause 17.1.1.2 Tissue #114 |
| Expected result 2. DUT sends SetURCBValues() response- 4. DUT sends SetURCBValues() response+ 8. DUT sends SetURCBValues() response+ |
| Test description 1. Client1 reserves an available URCB 2. Client2 configures the same URCB by requesting SetURCBValues() with one of the following attributes RptID, DatSet, OptFlds, BufTm, TrgOps, IntgPd 3. Client1 resets the reservation of the URCB 4. Client2 reserves and configures the URCB 5. Client2 resets the reservation of the URCB 6. Client1 reserves the URCB 7. Client1 aborts and re-establishes the association 8. Client1 configures the URCB 9. Client1 resets the reservation of the URCB |
| Comment |

| RpN6 | Configure unsupported URCB options | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1 IEC 61850-8-1 clause 17.1.1.2 |
| Expected result 1 to 3: DUT sends SetURCBValues() response- with error “object-value-invalid" |
| Test description 1. Client requests SetURCBValues() with one of the unsupported optional fields 2. Client requests SetURCBValues() with one of the unsupported trigger conditions 3. Client requests SetURCBValues() with one of the unsupported URCB parameters |
| Comment PIXIT specifies that the following optional fields are not supported: <to be completed> PIXIT specifies that the following trigger conditions are not supported: <to be completed> PIXIT specifies that the following RCB parameters are not supported: <to be completed> |

| RpN7 | Pre-assigned URCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1 IEC 61850-8-1 clause 17.1.1.2 |
| Expected result 1. DUT sends SetURCBValues() response- |
| Test description 1. Client configures an URCB that is pre-assigned to another client |
| Comment |

## A4.7	Buffered Reporting

Abstract test cases

|  | Request GetLogicalNodeDirectory(BRCB) and check response Request GetBRCBValues of all responded BRCB’s |
| --- | --- |
|  | Verify the reporting of optional fields of a BRCB Configure/enable a BRCB with all optional fields combinations: sequence-number, report-time-stamp, reason-for-inclusion, data-set-name, data-reference, buffer-overflow, and/or entryID (IEC 61850-7-2 clause 14.2.3.2.2.1), force/trigger a report and check the reports contain the enabled optional fields (7-1 clause 14.2.1) |
|  | Verify the trigger conditions of a BRCB Configure and enable a BRCB with optional fields: sequence-number, report-time-stamp, reason-for-inclusion, data-set-name, data-reference, buffer-overflow, and entryID and check the reports are transmitted according to the following (supported) trigger conditions: on integrity on update (dupd) on update with integrity on data change (dchg) on data and quality change on data and quality change with integrity period Verify the validity of the ReasonCode (IEC 61850-7-2 clause 14.2.3.2.2.9) Verify that when more trigger conditions are met preferably only one report is generated (IEC 61850-7-2 clause 14.2.3.2.3.2) Verify that reports are only sent when RptEna is set to True. (IEC 61850-7-2 clause 14.2.2.5), when reporting is disabled no reports should be transmitted |
|  | General interrogation Setting the GI attribute of a BRCB shall start the general-interrogation process. One report with the current data values will be sent. After initiation of the general-interrogation, the GI attribute is reset to False. (IEC 61850-7-2 clause 14.2.2.13) |
|  | Segmentation of reports Verify that if a long report does not fit in one message, the report is split into sub-reports. Enable sequence-number and report-time-stamp optional field and check validity of: (IEC 61850-7-2 clause 14.2.3.2.2.5) SeqNum (not changed) SubSeqNum (0 for first report, incrementing, roll-over) MoreSeqmentsFollow TimeOfEntry (not changed as SeqNum is not altered) (IEC 61850-7-2 clause 14.2.3.2.2.9) Verify that an update of a data value during sending of a segmented report caused by an integrity or general-interrogation trigger can be interrupted by a report with change of one of the data values with a new sequence number. (IEC 61850-7-2 clause 14.2.3.2.3.5) A new request for general-interrogation shall stop the sending of remaining segments of the GI-report that is still going on. A new GI-report shall start with a new sequence number and the sub-sequence number shall be 0 (IEC 61850-7-2 clause 14.2.3.2.3.4) |
|  | Configuration revision (IEC 61850-7-2 clause 14.2.2.7) Verify that ConfRev represents a count of the number of times the configuration of the data set referenced by DatSet has been changed. Changes that are counted are: deletion of a member of the data-set re-ordering of members in the data-set ConfRev should never be 0 (zero). Verify that after a restart of the server, the value of ConfRev remains unchanged (IEC 61850-7-2 clause 14.2.2.7) |
|  | Buffer Time (IEC 61850-7-2 clause 14.2.2.9) Verify that in the case where a second internal notification of the same member of a DATA-SET has occurred prior to the expiration of BufTm, the server: (IEC 61850-7-2 clause 14.2.2.9) shall for status information behave as if BufTm has expired and immediately send the report, restart the timer with value BufTm and process the second notification or may for analogue information behave as if BufTm has expired and immediately transmit the report for transmission, restart the timer with value BufTm and process the second notification or may for analogue information substitute the current value in the pending report with the new one. Configure Buffer Time to 1000 milliseconds and force a data value change of multiple dataset members within buffer time. Server should send not more than one report per buffer time with all the data values changes since last report. Verify that the value 0 for buffer time indicates that the buffer time attribute is not used. (IEC 61850-7-2 clause 14.2.2.9) Verify that the BufTm value can contain at least the value 3600000 (= one hour in milliseconds) |
|  | Buffered reporting (BRCB) state machine (IEC 61850-7-2 clause 14.2.2.5 figure 20) Verify events are buffered after the association is released Verify reporting is disabled after the association is lost Verify that not received reports while not associated are received now in the correct order (SOE) (IEC 61850-7-2 clause 14.2.1, IEC 61850-7-2 clause 14.2.2.5) Do the same but now set PurgeBuf to True before enabling the reporting. No stored buffered reports should be send (IEC 61850-7-2 clause 14.2.2.14) Verify that after changing DatSet, the report buffer is purged. (IEC 61850-7-2 clause 14.2.2.5) Force buffer overflow, the OptFlds buffer-overflow should be set in the first report that is sent with events that occurred after the overflow. (IEC 61850-7-2 clause 14 2.3.2.2.8) |
|  | Buffered reporting (BRCB); buffering events (IEC 61850-7-2 clause 14.2.3.2.3.6) Verify that after the association is available again and after the client has set the EntryID, and enabled the BRCB, the BRCB shall start sending the reports of events that have been buffered. The BRCB shall use the sequence and subsequence numbers so that no gaps occur. |
|  | Verify the DUT can send reports with data objects |
|  | Verify the DUT can send reports with data attributes |
|  | Verify that all buffered events shall be sent before integrity and GI reports can be sent (IEC 61850-7-2 clause 14.2.3.2.3.3) |
|  | Verify that when the LLN0 behaviour value changes from On to Off or Blocked no reports should be transmitted anymore for this logical device (IEC 61850-7-4 page 80) |

|  | Request GetBRCBValues with wrong parameters and verify response- service error (IEC 61850-7-2 clause 14.2.3.3.2) |
| --- | --- |
|  | Configure reporting but omit setting one of the trigger options (dchg, qchg, dupd, integrity). No reports should be send when generating events (IEC 61850-7-2 clause 14.2.3.2.2.9) |
|  | Setting the integrity period to 0 with TrgOps = integrity will result in no integrity reports will be sent (IEC 61850-7-2 clause 14.2.2.12) |
|  | Incorrect configuration of a BRCB: configure when enabled, configure ConfRev and SqNum and configure with unknown data set |
|  | Exclusive use of BRCB and lost association Configure a BRCB and enable it. Verify another client can not set attributes value in this BRCB. (IEC 61850-7-2 clause 14.2.1) |
|  | Configure unsupported BRCB options (PIXIT); Configure unsupported trigger conditions, optional fields and related parameters |
|  | Verify another client can not configure a pre-assigned BRCB |

Detailed test procedures

| Br1 | GetLogicalNodeDirectory(BRCB) and GetBRCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 9.2.2 and 14.2.3.3 IEC 61850-8-1 clause 12.3.1 and 17.2.2 |
| Expected result 1. DUT sends GetLogicalNodeDirectory(BRCB) response+ with a list of BRCB’s 2. DUT sends GetBRCBValues response+ |
| Test description 1. For each logical node Client requests GetLogicalNodeDirectory(BRCB) 2. For each BRCB Client requests GetBRCBValues() |
| Comment |

| Br2 | Reporting of optional fields for a BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.8 IEC 61850-8-1 clause 17.1.1.1, 17.2.1 PIXIT, Tissue #297 and #301 |
| Expected result 1. DUT sends SetBRCBValues response+ 2. DUT sends SetBRCBValues response+ 3. DUT sends a correct report according to trigger condition and IEC 61850-8-1 table 40 with all data set members for reason integrity and otherwise only the changed members. The configured and reported optional fields should match the sequence number is incremented and starts with 0 (Tissue #297 and #301) the report time stamp is in binary time format and matches the trigger time the reason for inclusion matches the trigger condition the configured and reported data set name do match the data-reference(s) match the data set member(s) buffer overflow is false EntryID as specified in the PIXIT Configuration revision matches the BRCB configuration When segmentation is set the report includes sub sequence number and more segments follow 4. DUT sends SetBRCBValues response+ and sends no reports anymore |
| Test description 1. Client configures an available BRCB using SetBRCBValues with all combinations of the following (supported) optional fields: sequence-number, report-time-stamp, reason-for-inclusion, data-set-name, data-reference, buffer overflow, entryID and conf-rev 2. Client enables the BRCB (set RptEna to True) 3. Client waits for a report (trigger condition integrity) or EQUIPMENT SIMULATOR triggers a report (trigger condition data change) 4. Client disables the BRCB (set RptEna to False) 5. Repeat step 1 to 4 for next combination of optional field |
| Comment PIXIT specifies the following optional fields are supported: <to be completed> |

| Br3 | Trigger conditions for a BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.8 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1, PIXIT |
| Expected result 1. DUT sends SetBRCBValues response+ for supported trigger conditions and response- when one of the trigger conditions isn’t supported 2. DUT sends SetBRCBValues response+ 3. DUT sends a report according to trigger condition integrity reports should be transmitted immediately at timeout data change reports are transmitted immediately when BufTm=0 data change reports are transmitted after BufTm of first data change when BufTm>0 4. The configured and reported optional fields should match 6. DUT does not sends reports |
| Test description 1. Configure an available BRCB using SetBRCBValues with all supported optional fields and one of the following (supported) trigger conditions: on integrity [on update (dupd)] [on update with integrity] on data and quality change on data and quality change with integrity period 2. Client enables the BRCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces several data changes of one or more data set members in the data set within/outside BufTm 4. Verify the reports are only transmitted according to trigger condition 5. Client disables the BRCB, set RptEna to False 6. EQUIPMENT SIMULATOR forces several data changes of one or more data set members in the data set within/outside BufTm 7. Repeat step 1 to 6 for next trigger condition combination |
| Comment PIXIT specifies the following trigger conditions are supported: integrity data/quality change |

| Br4 | General interrogation BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.8, 14.2.2.13 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1 |
| Expected result 3. DUT sends SetBRCBValues() response+ and then sends GI report 4. DUT sends GetBRCBValues() response+ with GI attribute not set |
| Test description 1. Client configures an available BRCB 2. Client enables the BRCB 3. Client requests SetBRCBValues() to set the GI report 4. Client requests GetBRCBValues() 5. Client disables the BRCB |
| Comment |

| Br5 | Segmentation of reports BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.8, 14.2.3.2.2.5, 14.2.3.2.2.9, 14.2.3.2.3.5, 14.2.3.2.3.4 IEC 61850-8-1 clause 8.1.3.8, 17.1.1.1, 17.2.1 PIXIT |
| Expected result 3. The segmented report messages have same SqNum, Incremented SubSeqNum starting with 0 and more segments follow is set and same EntryTime and EntryID |
| Test description 1. Create or use a pre-configured data set which reported values do not fit in one MMS PDU (reduce the MMS PDU size when necessary) 2. Client configures an available BRCB with the data set, with at least the optional fields sequence-number and report timestamp 3. Client enables the BRCB and verify the segmentation of (integrity) reports 4. Client disables the BRCB |
| Comment |

| Br6 | Configuration revision | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.7 IEC 61850-8-1 clause 17.2.1 |
| Expected result 2. DUT sends GetBRCBValues() response+ with ConfRev >0 4. The value of ConfRev is incremented |
| Test description 1. Client configures a BRCB to use a data-set Client request GetBRCBValues() Client configures the same BRCB with another data-set Client request GetBRCBValues() |
| Comment Test procedure is mandatory when datSet of RCB is dynamic see ICD. |

| Br7 | Buffer time | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.2.9 IEC 61850-8-1 clause 17.2.1, PIXIT |
| Expected result 3. On second data change in BufTm DUT sends the report of the first data change, and restarts the timer, at BufTm expiration DUT sends the report of the second data change On second data change in BufTm DUT sends the report of the first data change, restarts the timer and at BufTm expiration DUT sends the report of the second data change OR DUT substitutes the current value in the pending report with the new one and sends it at BufTm expiration. Verify the behaviour matches PIXIT DUT sends one report with both status events after BufTm expires DUT sends one report with both analogue events after BufTm expires 7. Each data change result in a report 8. DUT accepts BufTm value 3.600.000 |
| Test description 1. Client configures an available BRCB using SetBRCBValues with a valid BufTm and all supported optional fields with the trigger conditions: data change and quality change 2. Client enables the BRCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces two data changes of the same status data set element in the data set before expiration of BufTm 4. EQUIPMENT SIMULATOR forces two data changes of the same analogue data set element in the data set before expiration of BufTm 5. EQUIPMENT SIMULATOR forces one data change of two different status data set elements in the data set before expiration of BufTm 6. EQUIPMENT SIMULATOR forces one data change of two different analogue data set elements in the data set before expiration of BufTm 7. Client disables the BRCB, sets BufTm to zero; repeat step 2, 3 and 4 8. Client disables the BRCB, sets BufTm to 3.600.000 9. Client disables the BRCB |
| Comment |

| Br8 | Buffered reporting | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1, 14.2.2.14, 14.2.2.5, 14.2.3..2.2.8 IEC 61850-8-1 clause 17.2.1, PIXIT |
| Expected result 1 to 6: Events are buffered after the association is released / aborted and reporting is disabled 7. Not received reports while not associated are received now in the correct order 8. Not received reports while not associated are received now in the correct order 9. No stored buffered reports should be send 10. No stored buffered reports should be send 11. The Optional field buffer-overflow should be set in the first report that is sent with events that occurred after the overflow |
| Test description 1. Client configures an available BRCB with all supported optional fields with the trigger conditions: on data and quality change and BufTm 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes of different status data set members in the data set within BufTm 4. Client requests Release 5. EQUIPMENT SIMULATOR forces several more data changes 6. Client re-establishes the association and requests GetBRCBValues() 7. Client enables the BRCB 8. Repeat step 2-7, but Abort the association at step 4 9. Repeat step 2-7, but set PurgeBuf before between step 6 and 7 10. Repeat step 2-7, but change the data set name between step 6 and 7 11. Repeat step 2-7, but generate more data changes then the PIXIT buffer size at step 5. |
| Comment |

| Br9 | Buffered events | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.6 IEC 61850-8-1 clause 17.2.1, PIXIT Tissues #297 and #301 |
| Expected result 8. the BRCB shall start sending the reports of events that have been buffered starting with the next event after the event specified in EntryID (see the note in Clause 14.2.2.15). The BRCB shall use the sequence and subsequence numbers so that no gaps occur. |
| Test description 1. Client configures an available BRCB with all supported optional fields with the trigger condition: data change and BufTm 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes of different status data set members in the data set within BufTm 4. Client requests Release EQUIPMENT SIMULATOR forces several more data changes Client re-establishes the association and requests GetBRCBValues() Client set a valid EntryID in the BRCB Client enables the BRCB |
| Comment |

| Br10 | Report data objects (FCD) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.2 |
| Expected result 2. Verify the DUT does report the whole data object |
| Test description 1. Configure DUT to report on data change of one or more data objects 2. Change the data portion of one data object |
| Comment |

| Br11 | Report data attributes (FCDA) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2 IEC 61850-8-1 clause 17.2 |
| Expected result 2. DUT reports the “data” attribute. Verify that the “timestamp” and “quality” attribute are not sent 3. All attributes are reported 4. All attributes are reported |
| Test description 1. Configure DUT to report a change on one or more data attributes including the “data” attribute and “quality” attribute of the same data object. If the PIXIT indicates timestamps are supported as data set attributes, then configure the “timestamp” attribute for this object 2. Force a change of the data attribute value 3. Request a general interrogation 4. Wait for integrity report |
| Comment |

| Br12 | Send buffered events before integrity report | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.3 IEC 61850-8-1 clause 17.2 |
| Expected result 3. DUT does send 2 reports: first a report with the buffered data change event and then the integrity report |
| Test description 1. Client configures an available BRCB using SetBRCBValues with a valid BufTm, a valid IntgPd whose value is smaller than the BufTm value and all supported optional fields with the trigger conditions: data change and integrity 2. Client enables the BRCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces a data change in the data set 4. Client disables the BRCB |
| Comment |

| Br13 | Behaviour Off or Blocked stops reporting | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.3 IEC 61850-7-4 page 80 IEC 61850-8-1 clause 17.2 |
| Expected result 2. DUT sends reports 3. DUT should not report the process value change within the logical device 4. DUT sends reports 5. DUT should not report the process value change within the logical device 6. DUT sends reports |
| Test description Client configures an available BRCB with trigger condition “dchg” Client enables the BRCB, and force a process value data change Client send Operate with LLN0 Mode = Off, and force a process value data change Client send Operate with LLN0 Mode = On, and force a process value data change Client send Operate with LLN0 Mode = Blocked, and force a process value data change Client send Operate with LLN0 Mode = On, and force a process value data change Client disables the BRCB |
| Comment |

| Br14 | Send buffered events before GI | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.3.3 IEC 61850-8-1 clause 17.2 |
| Expected result 3. DUT does send 2 reports: first a report with the buffered data change event and then the general interrogation report |
| Test description 1. Client configures an available BRCB using SetBRCBValues with a valid BufTm and all supported optional fields with the trigger conditions: data change and general-interrogation 2. Client enables the BRCB, set RptEna to True 3. EQUIPMENT SIMULATOR forces a change in the data set and then the Client requests SetBRCBValues (GI=TRUE) before expiration of BufTm 4. Client disables the BRCB |
| Comment |

| BrN1 | Incorrect GetBRCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.3.2 IEC 61850-8-1 clause 17.2 |
| Expected result 1. See SrvN1 |
| Test description 1. Repeat SrvN1 for a GetBRCBValues |
| Comment |

| BrN2 | No trigger condition | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.2 |
| Expected result 1. DUT does not send reports when reporting is enabled and events are generated |
| Test description 1. Repeat Br3 with no trigger condition |
| Comment |

| BrN3 | Integrity period zero | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.2 |
| Expected result 4. DUT does not send integrity reports |
| Test description 1. Configure an available BRCB using SetBRCBValues with trigger condition Integrity and integrity period 0 2. Wait one minute 3. Client sets the BRCB RptEna to True (without synchronizing the BRCB by setting the BRCB EntryID) 4. Wait one minute 5. Client disables the BRCB |
| Comment |

| BrN4 | Incorrect configuration of BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.3.2.2.9 IEC 61850-8-1 clause 17.1.1.1 |
| Expected result 2. DUT sends SetBRCBValues() response with data access error “temporarily-unavailable” 4. DUT sends SetBRCBValues() response with data access error “object-access-denied” 5. DUT sends SetBRCBValues() response with data access error “object-value-invalid” |
| Test description 1. Client configures and enable an available BRCB 2. Client requests SetBRCBValues() with one of the following “dyn” attributes RptID, DatSet, OptFlds, BufTm, TrgOps, IntgPd, PurgeBuf, EntryID 3. Disable the BRCB 4. Client requests SetBRCBValues() with one of the following attributes ConfRev, SqNum, TimeOfEntry (when “fix” or “conf”) 5. Client requests SetBRCBValues() with unknown DatSet (when DatSet is “dyn”) |
| Comment |

| BrN5 | Exclusive use of BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1, 14.2.2.5 IEC 61850-8-1 clause 17.1.1.2 |
| Expected result 2. DUT sends SetBRCBValues() response- |
| Test description 1. Client1 configures and enables an available BRCB 2. Client2 configures the same BRCB by requesting SetBRCBValues() with one of the following attributes RptID, DatSet, OptFlds, BufTm, TrgOps, IntgPd, PurgeBuf, EntryID 3. Client1 disables the BRCB |
| Comment |

| BrN6 | Configure unsupported BRCB options | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1 IEC 61850-8-1 clause 17.1.1.1 |
| Expected result 1 to 3: DUT sends SetBRCBValues() response- with data access error “object-value-invalid" |
| Test description 1. Client requests SetBRCBValues() with one of the unsupported optional fields 2. Client requests SetBRCBValues() with one of the unsupported trigger conditions 3. Client requests SetBRCBValues() with one of the unsupported BRCB parameters |
| Comment PIXIT specifies that the following optional fields are not supported: <to be completed> PIXIT specifies that the following trigger conditions are not supported: <to be completed> PIXIT specifies that the following RCB parameters are not supported: <to be completed> |

| BrN7 | Pre-assigned BRCB | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 14.2.1 IEC 61850-8-1 clause 17.1.1.2 |
| Expected result 1. DUT sends SetBRCBValues() response- |
| Test description 1. Client configures an BRCB that is pre-assigned to another client |
| Comment |

A4.7+		Enhanced Buffered Reporting

Abstract test cases for tissue: 49, 190, 191, 275, 278, 297, 300, 322, 329, 335, 349 as specified in annex “Reporting Version7.zip” of  tissue #453

|  | Verify that integrity reports are buffered |
| --- | --- |
|  | Verify that the first report after RptEna is set to true always has SqNum=0 |
|  | Verify that BufOvl flag is set at the first report after the BRCB is enabled and reset at the following reports |
|  | Verify successful ResvTms behaviour On ResvTms = -1 the BRCB can be used by the configured client On ResvTms = 0 a client can reserve the BRCB by writing a value and configure the BRCB On lost association the reserved BRCB is released after the ResvTms number of seconds |
|  | Verify that a SetBRCBValues request, for setting ResvTms, shall: Generate a negative response if the BRCB’s ResvTms value is -1. Generate a negative response if the BRCB’s ResvTms value is non-zero and if the SetBRCBValues request is being issued by another client for whom the BRCB is not reserved. Generate a negative response if the ResvTms value to be set is negative. |
|  | Verify that TimeOfEntry and EntryID pair are consistent after restoring a lost association by setting the EntryID to zero to transmit the whole buffer again |
|  | Verify that a change of one of the following BRCB parameters purges the buffer: RptID, BufTm, TrgOps, IntgPd, DatSet. A change of OptFlds should not purge the buffer |
|  | Verify that after setting an invalid or non-existing EntryID the DUT sends all reports in the buffer |
|  | Verify that without the GI trigger condition the DUT does not send GI reports |
|  | Verify that when the BRCB state is RptEna=FALSE a GetBRCBValues shall return the EntryID value that represents the last (newest) entry that has been entered into the buffer. And when the BRCB RptEna=TRUE: The value of EntryID, returned in a GetBRCBValues response, shall be the EntryID of the last EntryID formatted and queued for transmission. |
|  | Verify that only the last buffered GI report is transmitted after restoring a lost association |
|  | Verify the DUT increments ConfRev when the BRCB datset is changed using SetBRCBValues() |

| BrE1 BrE2 BrE3 | Buffer integrity reports First report has Sequence number 0 BufOvl flag is set only at first report | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 1 to 6: Integrity reports are buffered after the association is released and reporting is disabled 3. and 7. First report after BRCB is enabled has sequence number 0 8. First report after BRCB is enabled has sequence number 0 and BufOvl=True, following reports have BufOvl=False |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and integrity with a valid integrity period 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes of different status data set members in the data set within BufTm 4. Client requests Release 5. EQUIPMENT SIMULATOR forces several more data changes 6. Client re-establishes the association and requests GetBRCBValues() 7. Client enables the BRCB 8. Repeat step 3 to 7 and but force a buffer overflow at step 5 |
| Comment |

| BrE4 | Successful BRCB reservation | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 1. DUT accepts configuration and send reports as configured 2. DUT accepts configuration and send reports as configured 4. DUT responds ResvTms = 0 |
| Test description 1. The pre-assigned client (compare ClientLN in SCL) configures and enables a pre-configured BRCB with ResvTms = -1 2. Client configures and enables a BRCB with ResvTms = 0 (no ClientLN in SCL) after it has set the ResvTms to a positive value 3. Client requests Release and wait 2 seconds longer then the ResvTms period 4. Client re-establishes the association and requests GetBRCBValues() |
| Comment |

| BrE5 | Failed BRCB reservation | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 1. DUT sends SetBRCBValues respond- 2. DUT sends SetBRCBValues respond- to Client2 3. DUT sends SetBRCBValues respond- |
| Test description 1. A non pre-assigned client configures a BRCB which is assigned to another client (ResvTms = -1) 2. Client1 reserves a BRCB with ResvTms = 0 by setting the ResvTms to a positive value. Client2 configures the same BRCB 3. Client set ResvTms=-1 on a BRCB with ResvTms = 0 |
| Comment |

| BrE6 | TimeOfEntry and EntryID | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 8. The matching EntryID’s in the reports send at step 3 and 8 have the same TimeOfEntry |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and integrity with a valid integrity period 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes of different status data set members in the data set within BufTm 4. Client requests Release 5. EQUIPMENT SIMULATOR forces several more data changes 6. Client re-establishes the association and requests GetBRCBValues() 7. Client sets the EntryID=0 8. Client enables the BRCB |
| Comment |

| BrE7 | Purge buffer | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 8..12. The buffer is purged, buffered reports are not transmitted 13. The buffer is NOT purged, buffered reports are transmitted |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and Integrity with a valid Integrity period 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes of different status data set members in the data set within BufTm 4. Client requests Release 5. EQUIPMENT SIMULATOR forces several more data changes 6. Client re-establishes the association and requests GetBRCBValues() 7. Client changes the RptID 8. Client enables the BRCB 9. Repeat step 3 to 8 and at step 7 client changes the BufTm 10. Repeat step 3 to 8 and at step 7 client changes the TrgOps 11. Repeat step 3 to 8 and at step 7 client changes the IntgPd 12. Repeat step 3 to 8 and at step 7 client changes the DatSet 13. Repeat step 3 to 8 and at step 7 client changes the OptFlds |
| Comment |

| BrE8 | Invalid EntryID | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 8. DUT responds with the EntryID value of the last Entry entered in the buffer 9. All reports in the buffer are transmitted (the BRCB transits from disabled to enabled state) |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and integrity with a valid integrity period 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes of different status data set members in the data set within BufTm 4. Client requests Release 5. EQUIPMENT SIMULATOR forces several more data changes 6. Client re-establishes the association and requests GetBRCBValues() 7. Client sets an invalid or unknown EntryID value 8. Client requests GetBRCBValues() 9. Client enables the BRCB |
| Comment |

| BrE9 | GI without GI trigger condition | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 3. DUT does not send the GI report 4. DUT responds GI=false |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and Integrity with a valid Integrity period, without GI 2. Client enables the BRCB (set RptEna to True) 3. Client sets GI=true 4. Client requests GetBRCBValues() |
| Comment |

| BrE10 | GetBRCBValues and EntryID | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 7. DUT responds the EntryID of the last entry that has been entered into the buffer (this value is different from the EntryID received in the last report) 8. DUT transmits the reports in the buffer (not transmitted before) 9. DUT responds the EntryID of last entry that has been formatted and queued for transmission 11. DUT responds the EntryID of the last entry that has been entered into the buffer 13. DUT responds the EntryID of the last entry that has been entered into the buffer 14. DUT transmits all reports in the buffer (including the reports transmitted before) 15. DUT responds the EntryID of last entry that has been formatted and queued for transmission |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and integrity with a valid integrity period 2. Client enables the BRCB (set RptEna to True) 3. EQUIPMENT SIMULATOR forces several data changes 4. Client requests Release 5. EQUIPMENT SIMULATOR forces several more data changes 6. Client re-establishes the association 7. Client request GetBRCBValues 8. Client enables the BRCB 9. Client request GetBRCBValues while DUT is sending buffered reports 10. Client disables the BRCB 11. Client request GetBRCBValues 12. Client sets EntryID = 0 13. Client request GetBRCBValues 14. Client enables the BRCB 15. Client request GetBRCBValues while DUT is sending buffered reports |
| Comment |

| BrE11 | GI reports not transmitted | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 3. DUT transmits the integrity reports and the GI reports 8. DUT transmits the old and new integrity reports and only the last GI report |
| Test description 1. Client configures a BRCB with all supported optional fields with the trigger condition data change and integrity with a valid integrity period 2. Client enables the BRCB (set RptEna to True) 3. Client requests GI report 3 times 4. Client requests Release and waits several integrity periods 5. Client re-establishes the association 6. Client sets EntryID to 0 7. Client request GetBRCBValues 8. Client enables the BRCB |
| Comment |

| BrE12 | DUT increments ConfRev when datset changes | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| TISSUE 453 |
| Expected result 4. DUT has incremented the ConfRev value in the BRCB 5. DUT transmits reports with the new ConfRev |
| Test description 1. Client request a GetBRCBValues() of a valid BRCB 2. Client disables the BRCB 3. Client changes the data set by deleting a dataset member or reordering dataset members. 4. Client request a GetBRCBValues() 5. Client enables the BRCB with optional field ConfRev |
| Comment |

## A4.8	Logging [Future]

Abstract test cases

| Test case | Test case description |
| --- | --- |
| Log1 | Request GetLogicalNodeDirectory(LOG) and check response+ |
| Log2 | Request GetLogicalNodeDirectory(LCB) and check response+ |
| Log3 | Request GetLCBValues with functional constraint LG of all responded LCB’s |
| Log4 | Request SetLCBValues with functional constraint LG when LCB is disabled |
| Log5 | Verify that logging is independent of a limited set of external application associations or other communication transactions |
| Log6 | Configure and enable logging and check that the following logging trigger conditions place a correct entry in the log with the correct members of the data set on integrity on update (dupd) on update with integrity on data change (dchg) on quality change (qchg) on data and quality change on data and quality change with integrity period |
| Log7 | Request QueryLogByTime and check response+ |
| Log8 | Request QueryLogByEntry and check response+ |
| Log9 | Request GetLogStatusValues and check response+, verify that the responded entries indicate the oldest/newest entry ID/time available in the log |

| Test case | Test case description |
| --- | --- |
| LogN1 | Request the following log services with wrong parameters (out of range entries, or non existent Dataset, LCB or Log) and verify response– service error GetLCBValues (IEC 61850-7-2 Subclause 14.3.2.5) SetLCBValues (IEC 61850-7-2 Subclause 14.3.2.6) QueryLogByTime (IEC 61850-7-2 Subclause 14.3.5.2) QueryLogByEntry (IEC 61850-7-2 Subclause 14.3.5.3) GetLogStatusValues (IEC 61850-7-2 Subclause 14.3.5.4) |
| LogN2 | Request SetLCBValues with functional constraint LG when LCB is enabled and verify response– service error |

The detailed test procedures will be completed in a future release of this document.

## A4.9	Generic Object Oriented Substation Events (GOOSE)

Compared to IEC 61850-10 the GSE test cases are defined for GOOSE and split in publish – subscribe – management.

Abstract test cases DUT publish

|  | Request GetLogicalNodeDirectory(GoCB) and request GetGoCBValues (IEC 61850-7-2 clause 15.2.2.5, clause 9.2.2) |
| --- | --- |
|  | GOOSE messages are published with a long cycle time, check the GOOSE data with configured data; (IEC 61850-7-2 clause 15.2.3) gocbRef is a valid GoCB reference timeAllowedtoLive > 0 and the next GOOSE message is transmitted within the specified value of the current GOOSE message datSet is same as the GoCB and contains a valid dataset reference goID is same as the GoCB and SCL, the default value is the GoCB reference t contains the time of the status increment or start-up sqNum is incremented, stNum>0 and isn’t changed test is not present or if present with value FALSE confRev >0 and is same as the GoCB and SCL (IEC 61850-7-2 clause 15.2.1.6) needsCommisioning is not present or if present same as GoCB numDatSetEntries matches with the number of data entries in allData allData values match with the datSet element type VID, priority and APPID as in SCL, CFI=0, TPID=0x8100 (IEC 61850-8-1 Annex C) |
|  | Verify that a newly activated device sends the initial GOOSE message with sqNum and stNum initial value one (1) (IEC 61850-7-2 clause15.1, 15.2.3.6+7) |
|  | Force a data change of a data value in the GOOSE dataset, DUT should publish GOOSE messages as specified/configured, stNum is incremented, sqNum = 0 |
|  | Enable test mode and verify that the test flag is set (IEC 61850-7-2 clause 15.2.3.8) |
|  | Disable GoCB, verify that changing parameters with SetGoCBValues are active (IEC 61850-7-2 clause 15.2.1.3, 15.2.2.5+6) and no Goose message are transmitted anymore |
|  | Verify that the Configuration revision matches SCL file ConfRev after DUT restart (IEC 61850-7-2 clause 15.2.1.6) |
|  | Verify that ConfRev represents a count of the number of times the configuration of the data set referenced by DatSet has been changed (IEC 61850-7-2 clause 15.2.1.6). Changes that are counted are: deletion of a member of the data-set re-ordering of members in the data-set changing the value of the attribute DatSet |
|  | Verify that NdsCom is set when DatSet is not yet configured (is NULL) (IEC 61850-7-2 clause 15.2.1.7) |
|  | Verify the DUT can send SendGOOSEmessage’s with data attributes and/or data objects |

|  | When GoEna=TRUE, no attributes of the GoCB control block can be set except for GoEna. (IEC 61850-7-2 clause 15.2.1.3) |
| --- | --- |
|  | Verify that if the number or size of values being conveyed by the elements in the dataset exceeds the SCSM determined maximum number, NdsCom is set to True. (IEC 61850-7-2 clause 15.2.1.7) |

Abstract test cases DUT subscribe

|  | Send single GOOSE message with/without the VLAN tag with new data and check if the message is received and the data has the new value by e.g. check binary output, event list, logging or MMI |
| --- | --- |
|  | Send single GOOSE message with the Test or NdsCom parameter set. Verify that on a status change the values are not used for operational purposes (IEC 61850-7-2 clause 15.2.3.8) |
|  | Proper detection and action roll-over of sqNum with no status change (sqNum=max -> sqNum = 1) and with status change (sqNum=max -> sqNum = 0) |
|  | DUT subscribes to a GOOSE with a dataset containing structured data (FCD) |

|  | Check behaviour of DUT as specified in PIXIT on Missing GOOSE message |
| --- | --- |
|  | Check behaviour of DUT as specified in PIXIT on Double GOOSE message |
|  | Check behaviour of DUT as specified in PIXIT on Delayed GOOSE message, with and without exceeding timeAllowedToLive |
|  | Check behaviour of DUT as specified in PIXIT on Out of order GOOSE message |
|  | Check behaviour of DUT as specified in PIXIT on No GOOSE messages |
|  | Check behaviour of DUT as specified in PIXIT on invalid GOOSE messages gocbRef different from GoCB and NULL timeAllowedtoLive = 0 datSet different from GoCB and NULL goID different from GoCB and NULL t contains the time of a status change minus/plus one hour confRev different from GoCB and NULL numDatSetEntries 0, more, less with the number of data entries in the allData allData values do not match with the datSet element type APPID different from SCL and 0 (IEC 61850-8-1 Annex C) |

Abstract test cases DUT management

| Gom1 | Verify GOOSE services: request service with legal parameters and check respond (IEC 61850-7-2 clause 15.2.2) GetGoReference (IEC 61850-7-2 clause 15.2.2.3) GetGOOSEElementNumber (IEC 61850-7-2 clause 15.2.2.4) |
| --- | --- |

| GomN1 | Services: request GOOSE service with illegal parameters and verify response- service error (IEC 61850-7-2 clause 15.2.2), Verify that NULL for MemberReference in GetGOOSEElementNumber indicates that no member of the referenced data set is defined. (IEC 61850-7-2 clause 15.2.2.4.2.2) |
| --- | --- |

Detailed test procedures

| Gop1 | GetLogicalNodeDirectory(GoCB) and GetGoCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.2.5 IEC 61850-8-1 clause 18.1.2.3 |
| Expected result 1. DUT sends GetLogicalNodeDirectory(GoCB) response+ with a list of GoCB’s. The object reference shall be “LDName/LLN0.GoCBName” 2. DUT sends GetGoCBValues response+ |
| Test description 1. For each logical node Client requests GetLogicalNodeDirectory(GoCB) 2. For each GoCB Client requests GetGoCBValues() |
| Comment: Conditional upon declaration of support for GetGoCBValues, GetLogicalNodeDirectory, and ServerSide Two-party association. |

| Gop2 | GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3.6+7 IEC 61850-8-1 clause |
| Expected result 1. DUT sends valid GOOSE messages with valid references, time stamp, incrementing sequence number, status number is the same |
| Test description 1. Force no data change. Wait for several GOOSE messages |
| Comment |

| Gop3 | Initial GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.3.2.2 IEC 61850-8-1 clause PIXIT |
| Expected result 1. DUT sends initial GOOSE message with stNum one (1) and sqNum as specified in the PIXIT |
| Test description 1. Restart the DUT, enable GoCB when necessary, and wait for initial GOOSE |
| Comment |

| Gop4 | GOOSE on data change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.3.2.2 IEC 61850-8-1 clause |
| Expected result 2. DUT sends GOOSE messages according to the configured retransmission strategy as, stNum is incremented, sqNum = 0 of the first message after data change |
| Test description 1. Force a data change of a data value in the GoCB data set 2. Wait for GOOSE messages |
| Comment |

| Gop5 | Test mode and test flag | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3.8 IEC 61850-8-1 clause 18.1.2.5 |
| Expected result DUT sends a GOOSE messages with test flag set DUT sends a GOOSE messages with test flag not set |
| Test description Test engineer enables test mode (Test flag = true in GOOSE header) Test engineer disables test mode |
| Comment |

| Gop6 | SetGoCBValues | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.3, 15.2.2.5, 15.2.2.6 IEC 61850-8-1 clause |
| Expected result DUT sends a SetGoCBValues response+ and stops transmitting GOOSE messages DUT sends a SetGoCBValues response+ and initializes/starts transmitting GOOSE messages. The first message has stNum=1. |
| Test description Client requests a SetGoCBValues with GoEna set to FALSE Client requests a SetGoCBValues with GoEna set to TRUE |
| Comment GoEna is the only attribute that may be written according to part 8-1. Conditional upon declaration of support for ServerSide TwoParty Association and SetGoCBValues. |

| Gop7a | Configuration revision matches SCL file contents | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.6, clause 15.2.3.9 IEC 61850-8-1 clause 18.1.1, 18.1.2.1, 18.1.2.4, 18.1.2.5, Annex A |
| Expected result 3). DUT restarts 4). DUT sends GOOSE message with ConfRev matching SCL file. |
| Test description SCL file for DUT is updated with new confRev value. Test engineer causes the DUT to be reconfigured with the SCL file. Test engineer restarts the DUT. DUT transmits GOOSE message. |
| Comment: |

| Gop7b | Configuration revision matches SCL file contents | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.6, clause 15.2.3.9 IEC 61850-8-1 clause 18.1.1, 18.1.2.1, 18.1.2.4, 18.1.2.5, Annex A |
| Expected result 2). DUT restarts 3). DUT sends a GetGoCBValues response+ with the same ConfRev (not null) value as configured in the SCL file. 4). DUT sends GOOSE message with the same ConfRev value as declared in the SCL file. |
| Test description Test engineer obtains SCL file containing DUT ConfRev. Test engineer restarts the DUT Client request GetGoCBValues(). Enable GoCB when necessary and wait for GOOSE message through SetGoCBValues() if PICS shows support. Otherwise, the DUT is expected to transmit the GOOSE. |
| Comment: This test is for those DUTs declaring support for GetGoCBValues and ServerSide TwoParty Association. PICS must show support for GetGoCBValues as well as SendGOOSE. |

| Gop8 | Configuration revision updates when associated DatSet is changed online | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.6 IEC 61850-8-1 clause |
| Expected result DUT sends a GetGoCBValues response+ with incremented ConfRev value DUT sends GOOSE message with incremented ConfRev value |
| Test description Test engineer deletes the first member of the GoCB data set in the SCL file. Test engineer causes the DUT to be reconfigured with the SCL file. Client requests a GetGoCBValues() Client waits for GOOSE message Test engineer re-orders the first and last member of the GoCB data set through the SCL file; repeat step 2-4 Test engineer changes the value of the GoCB data set through the SCL file; repeat step 2-4 |
| Comment: Conditional on declaration of support for: GetGoCBValues, SetGoCBValues, and ServerSide TwoParty Association. |

| Gop9a | Ensure that NULL data sets are not sent. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1 Tissue #333, PIXIT |
| Expected result 3. DUT Restarts 5. DUT shall not send a GOOSE for the GOCB message or sets NdsComm per PIXIT. |
| Test description Test engineer changes an SCL file to have a NULL data set reference in a GoCB. Test engineer causes the DUT to be reconfigured with the SCL file. Test engineer restarts DUT. Test engineer, if needed, uses some means to attempt to enable the GOCB. Wait 1 minute. |

| Gop9b | Ensure that NULL data sets are either refused or result in NdsCom=TRUE. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1 Tissue #333, PIXIT |
| Expected result 3. DUT restarts 4. DUT sends SetGoCBValues response+ or – depending upon PIXIT declaration. 5. DUT sends a GetGoCBValues response+ with NdsCom=TRUE conditional upon support for GetGoCBValues being declared and GoCB.enable = TRUE. 6. DUT does not send GOOSE message for GOCB that has a NULL DatSet value message or sets NdsComm per PIXIT. |
| Test description 1. Test engineer changes an SCL file to have a NULL data set reference in a GoCB. 2. Test engineer causes the DUT to be reconfigured with the SCL file. 3. Test engineer restarts DUT. 4. Test engineer enables GoCB using SetGoCBValues. 5. Client requests a GetGoCBValues() 6. Wait one minute. |
| Comment: This test is for DUTs that declare support for GetGoCBValues ,SetGoCBValues, and ServerSide TwoParty Association. |

| Gop10 | GOOSE with data attributes (FCDA) and data objects (FCD) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2 IEC 61850-8-1 clause 18.1 PIXIT |
| Expected result 1. DUT sends a GOOSE messages with data attributes 2. DUT sends a GOOSE messages with data objects |
| Test description Verify the DUT is able to send GOOSE message with data attributes (FCDA) Verify the DUT able to send GOOSE message with data objects (FCD) |
| Comment: Conditional upon declaration of support of FCDs as data set members. |

| GopN1 | Verify that GoCB components are read-only | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.2.3, 15.2.2.4 IEC 61850-8-1 clause 18.1, Table 50, PIXIT |
| Expected result DUT sends a SetGoCBValues response- DUT sends a SetGoCBValues response- DUT sends a SetGoCBValues response- According to PIXIT (DUT sends a SetGoCBValues response+) |
| Test description Client requests a SetGoCBValues with valid GoID Client requests a SetGoCBValues with valid DatSet Client requests a SetGoCBValues with valid DstAddress Client requests a SetGoCBValues to enable/disable GoEna |
| Comment Table 50 in 8-1 specifies that only GoEna can be written, other components are read-only |

| GopN2a | Ensure behaviour of GOOSE when data set contents are too large. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1 PIXIT |
| Expected result 1. DUT Restarts 3. DUT does not send GOOSE message or sets NdsComm per PIXIT. |
| Test description Test engineer activates the DUT that has a GoCB configured with a data set that is too large for GOOSE (configuration through an SCL file). Test engineer enables, through local means, the GoCB if needed. Test engineer waits 1 minute. |
| Comments: Conditional upon support for PIXIT ability to have user defined DatSet values. |

| GopN2b | Ensure behaviour of GOOSE when data set contents are too large. | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1.7 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result 1. DUT Restarts 2. DUT responds with one of the following, per PIXIT: SetGoCBValues response- or SetGoCBValues response+ 3. GetCoCBValues returns: For (2) Response+: GoEna=TRUE and NdsCom= TRUE; For (2) Response-: GoEna=FALSE and NdsCom= TRUE. 4. DUT does not send the GOOSE message or sets NdsComm per PIXIT. |
| Test description Test engineer activates the DUT that has a GOCB configured with a data set that is too large for GOOSE. Test engineer uses SetGoCBValues to enable the GOCB. Test engineer uses GetGoCBValues to determine state of GoCB. Test engineer waits 1 minute. |
| Conditional upon support for SetGoCBvalues , GetGoCBValues, ServerSide Two Party Association, and PIXIT ability to use non-predefined DataSets. |

DUT subscribe

To perform the DUT subscribe test procedures the DUT need to be configured as follows

- a data value that is connected to a subscribed GOOSE member, e.g. GGIO.SPS01

- a data set that contains the value of this data point

- a GoCB that publishes the (changed) value(s) in the data set

As such the analyzer trace file contains the proof when the subscribed GOOSE messages is processed.

| Gos1 | Subscribe GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1 |
| Expected result DUT updates the value and sends a GOOSE message or Report with changed status value |
| Test description Test engineer configures the DUT with subscribed GOOSE Publisher sends GOOSE message with new data value with the VLAN tag Publisher sends GOOSE message with new data value without the VLAN tag |
| Comment |

| Gos2 | Subscribe GOOSE with Test or NdsCom set | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result Compare PIXIT DUT ignores the data value change |
| Test description Test engineer configures the DUT as specified Publisher sends GOOSE message with new data value with Test set Publisher sends GOOSE message with new data value with NdsCom set |
| Comment |

| Gos3 | SqNum roll-over with/without status change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result DUT just receives the messages without any action DUT just receives the messages without any action DUT responds to the status change |
| Test description Publisher sends GOOSE message with sqNum = max–1, max and 1 without status change Publisher sends GOOSE message with sqNum = max–1, max Publisher forces a status change stNum and sends a GOOSE message with incremented stNum and sqNum=0 |
| Comment |

| Gos4 | Subscribe to data set with structured data (FCD) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result DUT responds to the status change |
| Test description Publisher sends GOOSE message with structured data Publisher sends GOOSE message with a data change in a data attribute in the structured data |
| Comment PIXIT specifies to which structured data the DUT can subscribe. |

| GosN1 | Missing GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result DUT accepts GOOSE message as specified in the PIXIT, resulting in a report or published GOOSE message |
| Test description Test engineer configures the DUT as specified Publisher sends correct GOOSE message with no value changes (same stNum) Publisher sends GOOSE message with data value change with incremented stNum, starting with sqNum=1 (simulating a missing sqNum=0) |
| Comment |

| GosN2 | Double GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1 |
| Expected result DUT accepts first GOOSE message, resulting in a report or published GOOSE message and ignores the second message with sqNum=0 |
| Test description Test engineer configures the DUT as specified Publisher sends correct GOOSE message with no value changes (same stNum) Publisher sends GOOSE message with data value change with incremented stNum, and with sqNum=0 two times (simulating a double sqNum=0) |
| Comment |

| GosN3 | Delayed GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1 |
| Expected result DUT behaves as specified in the PIXIT |
| Test description Test engineer configures the DUT as specified Publisher sends correct GOOSE message with no value changes (same stNum) Publisher sends GOOSE message with data value change with incremented stNum, and with sqNum=0, but outside the TimeAllowedtoLive interval of the previous GOOSE message. The following GOOSE messages with sqNum>0 are transmitted inside the TAL of the previous message. |
| Comment |

| GosN4 | Out-of-order GOOSE message | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result DUT behaves as specified in the PIXIT |
| Test description Test engineer configures the DUT as specified Publisher sends correct GOOSE message with no value changes (same stNum) Publisher sends GOOSE message with data value change with incremented stNum, and with sqNum=1, sqNum=0, sqNum=2,3 etc. |
| Comment |

| GosN5 | No GOOSE message received with publication continuing | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.3 IEC 61850-8-1 clause 18.1, PIXIT |
| Expected result DUT indicates that subscribed GOOSE message isn’t received (PIXIT) DUT indicates that subscribed GOOSE message is received . DUT indicates that subscribed GOOSE message isn’t received (PIXIT) DUT should process new state value(s). |
| Test description Test engineer configures the DUT as specified Publisher sends correct GOOSE message with no value changes (same stNum) Publisher is disconnected from the network, continues to send GOOSE messages for 30 seconds with no state change (e.g. same stNum as step 2). Publisher is reconnected to the network and continues to send GOOSE messages (same stNum) Publisher is disconnected from the network, continues to send GOOSE messages for 30 seconds with no state change (e.g. same stNum as step 2). Publisher is reconnected to the network and continues sends GOOSE messages indicating a state change (incremented stNum, sqNum other than 0) |
| Comment |

| GosN6 | GOOSE message does not match DUT SCL configuration | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.1, 15.2.3 IEC 61850-8-1 clause 18.1, Annex C, PIXIT |
| Expected result DUT responds as specified in the PIXIT |
| Test description Test engineer configures the DUT as specified below and Publisher sends several GOOSE messages with data value change with correct status and sequence numbers with an initial or stNum change: GoCB reference = mismatch with expected GoCB from SCL , NULL timeAllowedtoLive = 0 datSet reference = mismatch with GoCB from SCL, NULL goID reference = mismatch with GoCB from SCL, NULL timestamp of status change = plus one hour, minus one hour, 0 confRev = mismatching with GoCB from SCL numDatSetEntries does not match the expected number of DataSet element members as configured by SCL. The confRev remains as expected, but the numDatSetEntries changes +1 or -1 and the allData matches the number of numDatSetEntries. values of allData entries(same DatSetReference, same expected ConfRev) = out-of-order APPID = different from SCL and 0 |
| Comment |

DUT management

| Gom1 | GetGoReference, GetGOOSEElementNumber | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.2.3+4 IEC 61850-8-1 clause 18 |
| Expected result DUT sends a GetGoReference response+ with the member reference DUT sends a GetGOOSEElementNumber response+ with the same member offset as the GetGoReference() request |
| Test description Client requests a GetGoReference() for first member offset Client requests a GetGOOSEElementNumber for responded member reference Repeat 1 and 2 for next member offset in the GoCB |
| Comment |

| GomN1 | Wrong parameters | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 15.2.2.3, 15.2.2.4 IEC 61850-8-1 clause 18.1 |
| Expected result DUT sends a GetGoReference response- DUT sends a GetGoReference response+ with a NULL reference and 2 correct references DUT sends a GetGoReference response+ with 2 correct references and a NULL reference DUT sends a GetGOOSEElementNumber response+ with 2 correct MemberOffset and a NULL offset- DUT sends a GetGOOSEElementNumber response- |
| Test description Client requests a GetGoReference with unknown GoCBReference and MemberOffset 1 Client requests a GetGoReference with MemberOffset 0, 1 and 2 Client requests a GetGoReference with MemberOffset n-1, n, n+1 (n is the number of elements in the dataset) Client requests a GetGOOSEElementNumber with 2 known and 1 unknown GoCBReference Client requests a GetGOOSEElementNumber with unknown MemberReference |
| Comment |

## A4.10	Control

Abstract test cases

|  | Force and check each path in control state machine for several control objects with control modes direct with normal security (IEC 61850-7-2 clause 17.2.1) SBO-control with normal security (operate once/many) (IEC 61850-7-2 clause 17.2.2) direct with enhanced security (IEC 61850-7-2 clause 17.3.2) SBO-control with enhanced security (operate once/many) (IEC 61850-7-2 clause 17.3.3) Compare detailed state machine test cases for each control mode |
| --- | --- |
|  | Verify that with test flag set no operations to the process are performed. |
|  | Select all SBO control objects and cancel them in opposite order |
|  | Time Operate a second enhanced security control object before the activation time of the first control object |
|  | Change control model using online services >> not applicable for part 8-1 |
|  | Enable/disable command termination using online services >> not applicable for part 8-1 |
|  | Verify that with specified check conditions the supported checks are performed and the command is executed accordingly (IEC 61850-7-2 clause 17.5.2.5) |

|  | Operate (without select) for a SBO control object and verify the response- and AddCause (IEC 61850-7.2 clause 17.2.2) |
| --- | --- |
|  | Select twice, second select should fail and verify the response- and AddCause (IEC 61850-7-2 clause 17.2.2) |
|  | Operate value is the same as the actual value (On-On, or Off-Off) and verify the response- and AddCause (IEC 61850-7-2 clause 17.2.2) |
|  | Select the same control object from 2 different clients, verify the response- and AddCause (IEC 61850-7-2 clause 17.2.2) |
|  | Select / Operate an unknown control object and verify the response- and AddCause (IEC 61850-7-2 clause 17.2.2) |
|  | Verify situations to set specific other applicable AddCause values (IEC 61850-7-2 clause 17.5.2.6) |
|  | Select an direct operate control object >> not applicable for part 8-1 |
|  | Operate a direct control object twice from 2 clients |
|  | Operate with different value then the SelectWithValue of a SBOes control object |
|  | Verify that on LLN0 behaviour Off or Blocked controls are rejected (IEC 61850-7-4 page 80) |
|  | Verify that when the IED is in Local operation remote controls are rejected (IEC 61850-7-2 table 40) |

Note: For direct and SBO with normal security the PIXIT specifies if the DUT will send an additional MMS InformationReport with LastApplError before the select/operate respond-. In that case the AddCause value should be the same as for enhanced security control

Detailed test procedures

| Ctl2 | Operate with test flag set | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.5.2.4 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result DUT sends all messages without executing the control action, as specified in the PIXIT |
| Test description DOns; Client sends correct Operate request with the Test flag set SBOns, Client sends correct Select and Operate request with the Test flag set DOes, Client sends correct Operate request with the Test flag set SBOes, Client sends correct SelectWithValue with the Test flag set and Operate with the Test flag set |
| Comment This behaviour will change in edition 2 of 61850-7-2 |

| Ctl3 | Select/Cancel all SBO control objects | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2 IEC 61850-8-1 clause 20, Annex E PIXIT |
| Expected result DUT sends response+ for non-interlocked objects and response- with AddCause "1-of-n control " for interlocked objects (PIXIT) |
| Test description Client request SelectWithValue for some SBOes control objects Client requests Select for some SBOns control objects Client request Cancel for the selected control object in reverse order |
| Comment |

| Ctl4 | Activate second time activated control object | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2 |
| Expected result DUT responds according to state machine |
| Test description TimeActivatedOperate a second enhanced security control object before the activation time of the first control object has expired |
| Comment |

| Ctl7 | Check conditions | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.5.2.5 |
| Expected result The supported check conditions are checked and command is executed when check passed. The command is not executed when the check failed and for the enhanced control models the DUT returns AddCause = “Blocked-by-interlocking” or “Blocked-by-synchrocheck” |
| Test description DOns; Client sends correct Operate request with both Check conditions set SBOns, Client sends correct Select and Operate request with both Check conditions set DOes, Client sends correct Operate request with both Check conditions set SBOes, Client sends correct SelectWithValue with both Check conditions set and Operate with both Check conditions set Execute each test with check result passed and failed. |
| Comment |

| CtlN1 | Direct operate a SBO control object | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result b) DUT responds with Operate response- and the control object stays in the “unselected” state d) DUT responds with Operate response- with AddCause “object-not-selected” and the control object stays in the “unselected” state |
| Test description b) Client sends correct Operate once request of an unselected SBOns object d) Client sends correct Operate once request of an unselected SBOes object |
| Comment |

| CtlN2 | Select a SBO control object twice | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 PIXIT |
| Expected result b) SBOns: DUT responds with Select response+ DUT responds with Select response- (recommended) or reset of select timeout (Note: TISSUE #334 solved 2008-08 specifies “Select response-“. IEC 61850 edition 2 will make this the only allowed response.) DUT responds with Operate response+ d) SBOes: DUT responds with SelectWithValue response+ DUT responds with SelectWithValue response- (recommended) or reset of select timeout (Note: TISSUE #334 solved 2008-08 specifies “Select response-“. IEC 61850 edition 2 will make this the only allowed response.) DUT responds with Operate response+ and CommandTermination+ |
| Test description b) SBOns: Client sends correct Select request of an unselected SBOns object Same client sends correct Select request of the same SBOns object just before the sboTimeout Client sends correct Operate request just before the sboTimeout of step 8 d) SBOes: Client sends correct SelectWithValue request of an unselected SBOes object Same client sends correct SelectWithValue request of the same SBOes object just before the sboTimeout Client sends correct Operate request just before the sboTimeout of step 2 |
| Comment |

| CtlN3 | SelectWithValue or Operate value is same as actual value | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 PIXIT |
| Expected result DUT responds as specified in PIXIT DUT responds as specified in PIXIT DUT responds as specified in PIXIT DUT responds as specified in PIXIT |
| Test description DOns: Client sends Operate request with actual value of a DOns object SBOns: Client sends Select and Operate request with actual value of a SBOns object DOes: Client sends Operate request with actual value of a DOes object SBOes: Client sends SelectWithValue request with actual value of a SBOes object, on response+ request Operate with actual value |
| Comment |

| CtlN4 | Select an SBO control object twice from 2 clients | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result b) SBOns: DUT responds with Select response+ DUT responds with Select response- DUT responds with Operate response+ d) SBOes: DUT responds with SelectWithValue response+ DUT responds with SelectWithValue response- with Error “Operator Test Not OK” and AddCause “Command-already-in-execution” DUT responds with Operate response+ and CommandTermination+ |
| Test description b) SBOns: Client1 sends correct Select request of an unselected SBOns object Client2 sends correct Select request of the same SBOns object before the sboTimeout Client1 sends correct Operate request d) SBOes: Client1 sends correct SelectWithValue request of an unselected SBOes object Client2 sends correct SelectWithValue request of the same SBOes object before the sboTimeout Client1 sends correct Operate request |
| Comment |

| CtlN6 | Force other AddCause values | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8, table 78 PIXIT |
| Expected result DUT responds with specific supported AddCause value as specified in the PIXIT |
| Test description Repeat one or more of previous test procedures, but now force a specific supported AddCause situation as specified in the PIXIT not supported block by switching hierarchy select-failed invalid position position reached parameter-change in execution step-limit blocked by mode blocked by process blocked by interlocking blocked by synchrocheck command already in execution blocked by health 1-of-n control abortion by cancel time limit over Abortion by trip Object-not-selected |
| Comment PIXIT specifies the support of the following AddCause values: <to be completed> The following AddCause values have been tested: <to be completed> |

| CtlN8 | Operate a direct control object twice from 2 clients | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 PIXIT |
| Expected result a) DOns DUT responds with Operate response+ DUT responds as specified in PIXIT c) DOes DUT responds with Operate response+ and CommandTermination+ DUT responds as specified in PIXIT |
| Test description a) DOns Client1 sends correct Operate request of a DOns object Client2 sends correct Operate request of the same DOns object within 5 milliseconds c) DOes Client1 sends correct Operate request of a DOes object Client2 sends correct Operate request of the same DOes object within 5 milliseconds |
| Comment |

| CtlN9 | Operate with different value then the SelectWithValue of a SBOes control object | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result 1. DUT responds with SelectWithValue response+ 2. DUT responds with Operate response- with error “Operator Test Not OK” and AddCause “Parameter-change-in-execution”. The control object will return to the unselected state |
| Test description Client sends correct SelectWithValue request of an unselected SBOes object Client sends Operate request of the selected object setting one of the following attributes to another value then the SelectWithValue: ctlVal, origin, ctlNum, test and Check Wait until control object returns to the “unselected state” |
| Comment |

| CtlN10 | Control an object when the associated Logical Node or LLN0 is not operable | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3, IEC 61850-7-4 page 80 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 PIXIT |
| Expected result a). DUT responds with Operate response- b) DUT responds with Select response-. The control object will return to the unselected state c) DUT responds with Operate response- with error “Operator Test Not OK” and AddCause “Blocked-by-Mode”. d) DUT responds with SelectWithValue or Operate response- with error “Operator Test Not OK” and AddCause “Blocked-by-Mode”. The control object will return to the unselected state |
| Test description Client sets the associated logical node Mode = Off or Blocked Client sends DOns – Operate request Client sends SBOns – Select request Client sends DOes – Operate request Client sends SBOes – SelectWithValue request, on response+ request Operate Repeat for the associated logical node Mode = On and LLN0.Mod = Off or Blocked |
| Comment |

| CtlN11 | Control an object when the IED is in Local operation | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.5.2.6, table 40 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 PIXIT |
| Expected result a) DUT responds with Operate response- b) DUT responds with Select response-. The control object will return to the unselected state c) DUT responds with Operate response- with error “Operator Test Not OK” and AddCause “Blocked-by-switching-hierarchy”. d) DUT responds with SelectWithValue or Operate response- with error “Operator Test Not OK” and AddCause “Blocked-by-switching-hierarchy”. The control object will return to the unselected state |
| Test description Test engineer sets the local/remote switch on the DUT to “Local” (LLN0.Loc=True) Client sends DOns – Operate request Client sends SBOns – Select request Client sends DOes – Operate request Client sends SBOes – SelectWithValue request, on response+ request Operate |
| Comment |

### A4.10a		Control DOns

|  | Path Operate Request[test ok] resp+ Perform a correct Operate request |
| --- | --- |
|  | Path TimeActivatedOperate Request [test ok] resp+ Client requests TimeActivatedOperate resulting in Test not ok |
|  | Path Operate Request[test not ok] resp- Client requests Operate resulting in Test not ok |
|  | Path TimeActivatedOperate Request[test ok] + TimerExpired[test ok] resp+ Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test Ok'. Verify the WaitForActionTime results in a timer expired ‘Test ok’ |
|  | Path TimeActivatedOperate Request[test ok] + TimerExpired[test not ok] resp- Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test Ok'. Force situation that the WaitForActionTime results in a timer expired ‘Test not ok’ |

Detailed test procedures for DOns

Note: The TimeActivatedOperate detailed test procedures are not defined in this version.

| DOns1 | Operate, test ok | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.1 IEC 61850-8-1 clause 20.7 |
| Expected result DUT responds with Operate response+ |
| Test description Client sends correct Operate request |
| Comment |

| DOns3 | Operate, test not ok | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.1 IEC 61850-8-1 clause 20.7 PIXIT |
| Expected result 1. DUT responds with Operate response-. This response may optionally be proceeded by a AddCause InformationReport. |
| Test description 1. Client requests Operate forcing a “test not ok” as specified in PIXIT |
| Comment |

### A4.10b	Control SBOns

|  | Path 1 Select request[test not ok] resp-: Select the device using Select with improper access rights. Verify the device returns to the Unselected state. |
| --- | --- |
|  | Path Select request[test ok] resp+: Select device correctly using Select Verify each of these paths will return the device to the Unselected state: Client requests Cancel Client waits for timeout Client requests TimeActivatedOperate resulting in Test not ok Client requests Operate resulting in Test not ok Client requests correct Operate Once |
|  | Path Select request[test ok] resp+ and TimeActivatedOperate request[test ok] resp+: Select device correctly using Select Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test Ok'. Verify each of these paths will return the device to the Unselected state: Force situation that the WaitForActionTime results in a timer expired ‘Test not ok’ Verify the WaitForActionTime results in a timer expired ‘Test ok, operate once’ |
|  | Path Select request[test ok] resp+ and Operate request[test ok, OPERATE MANY] resp+: Select device correctly using Select Verify that sending a correct Operate Many request will return the device to the Ready state |
|  | Path Select request[test ok] resp+ and TimeActivatedOperate request[test ok] resp+ and TimerExpired[test ok, OPERATE MANY] resp+: Select device correctly using Select Send a correct TimeActivatedOperate Many request After the timer has expired, verify the device returns to the Ready State |

Detailed test procedures for SBOns

| SBOns1 | Incorrect Select | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2 IEC 61850-8-1 clause 20.4 and 20.7 |
| Expected result DUT sends a Select response- (MMS read response+ with SBO null value) |
| Test description Client sends Select request with unknown control object |
| Comment |

| SBOns2 | Select followed by Cancel, timeout or Operate resulting in test not ok | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2 IEC 61850-8-1 clause 20.4 and 20.7 |
| Expected result DUT responds with Cancel response+ DUT sends nothing DUT responds with a TimeActivatedOperate response- with AccessResult indicating failure as defined in IEC 61850-8-1 table 72 DUT responds with an Operate response- with AccessResult indicating failure as defined in IEC 61850-8-1 table 72. This response may optionally be proceeded by an AddCause InformationReport. DUT responds with an Operate response+ In all cases the control object returns to the “unselected” state |
| Test description Client sends correct Select request followed by: Client sends correct Cancel request Or Client waits for timeout Or force EQUIPMENT SIMULATOR that the Client TimeActivatedOperate request results in “test not ok” Or force EQUIPMENT SIMULATOR that the Client Operate request results in “test not ok” Client sends correct Operate request |
| Comment |

| SBOns3 | Select, TimeActivatedOperate once followed by failed wait for action time or cancel | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2 IEC 61850-8-1 clause 20.4 and 20.7 |
| Expected result DUT responds with Select response+ DUT responds with TimeActivatedOperate response+ DUT responds nothing DUT responds with Cancel response+ In all cases the control object returns to the “unselected” state |
| Test description Client sends correct Select request Client sends correct TimeActivatedOperate once request During wait time force EQUIPMENT SIMULATOR to create an interlock resulting in wait for action time – test not ok Or Client sends correct Cancel request |
| Comment |

| SBOns4 | Select and Operate many | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2 IEC 61850-8-1 clause 20.4 and 20.7 |
| Expected result In all cases the control object returns to the “ready” state |
| Test description Repeat SBOns2, but set the control object sboClass to “operate-many” |
| Comment |

| SBOns5 | Select, TimeActivatedOperate many | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.2.2 IEC 61850-8-1 clause 20.4 and 20.7 |
| Expected result In all cases the control object returns to the “ready” state |
| Test description Repeat SBOns2, but set the control object sboClass to “operate-many” |
| Comment |

### A4.10c		Control DOes

|  | Path TimeActivatedOperate request[test not ok] resp-: Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test not Ok'. |
| --- | --- |
|  | Path Operate request[test not ok] resp-: Send an Operate request, thereby making sure the device will generate a 'test not Ok'. |
|  | Path TimeActivatedOperate request[test ok] resp+: Send a correct TimeActivatedOperate request Verify each of these paths will return the device to the Ready state: Client waits for timeout (test not ok) Client requests correct Cancel |
|  | Path TimeActivatedOperate request[test ok] resp+ and Timer expired [test ok] resp+: Send a correct TimeActivatedOperate request Verify the WaitForActionTime results in a timer expired ‘Test ok’ After the timer has expired, verify each of these paths will return the device to the Ready state: The output of the device moves to its new state, resulting in a state new, CommandTermination+ Force the output of the device such that the output keeps its old state, resulting in a state old, CommandTermination- Force the output of the device such that the output keeps reaches the 'between' state, resulting in a state between, CommandTermination - |
|  | Path Operate request[test ok] resp+: Send a correct Operate request After the timer has expired, verify each of these paths will return the device to the Ready state: The output of the device moves to its new state, resulting in a state new, CommandTermination+ Force the output of the device such that the output keeps its old state, resulting in a state old, CommandTermination- Force the output of the device such that the output keeps reaches the 'between' state, resulting in a state between, CommandTermination- |

Detailed test procedures for DOes

Note: The TimeActivatedOperate detailed test procedures are not defined in this version.

| DOes2 | Operate test not OK | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.7 and 20.8 PIXIT |
| Expected result DUT responds with Operate response- with LastApplError with error “Operator Test Not OK” and AddCause as specified in PIXIT |
| Test description Client sends incorrect Operate once request |
| Comment |

| DOes5 | Operate once followed by new, old and in between state change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.7 and 20.8 |
| Expected result DUT responds with Operate response+ DUT reports CommandTermination+ After timeout DUT reports CommandTermination- with error “Timeout Test Not OK” and AddCause “Invalid position” or “Time-limit-over” After timeout DUT reports CommandTermination- with error “Timeout Test Not OK” and AddCause “Invalid position” |
| Test description Client sends correct Operate once request followed by Force EQUIPMENT SIMULATOR to go to the new state Or force EQUIPMENT SIMULATOR to keep the old state Or force EQUIPMENT SIMULATOR to go to the in between state |
| Comment |

### A4.10d	Control SBOes

|  | Path 1 (returning to Unselected state): Select device using SelectWithValue with improper access rights. Access should be denied (IEC 61850-7-2 clause 17.2.2) |
| --- | --- |
|  | Path 2+3a/b/c/d (returning to Unselected state): Select device correctly using SelectWithValue Verify each of these paths will return the device to the Unselected state: Client requests Cancel (3a) Client waits for timeout (3b) Client requests TimeActivatedOperate resulting in Test not ok (3c) Client requests Operate resulting in Test not ok (3d) |
|  | Path 2+4+8a/b/c (returning to Unselected state): Select device correctly using SelectWithValue Verify each of these paths will return the device to the Unselected state: Perform a correct Operate Once request (8a) Perform a correct Operate Once request and force the output of the device such that the output keeps its old state (8b) Perform a correct Operate Once request and force the output of the device such that the output keeps reaches the 'between' state (8c) |
|  | Path 2+5+6 (returning to Unselected state): Select device correctly using SelectWithValue Send a TimeActivatedOperate request, thereby making sure the device will generate a 'test Ok'. Force situation that the WaitForActionTime results in a timer expired ‘Test not ok’ |
|  | Path 2+5+7+8a/b/c (returning to Unselected state): Select device correctly using SelectWithValue Send a correct TimeActivatedOperate request Verify the WaitForActionTime results in a timer expired ‘Test ok’ After the timer has expired, verify each of these paths will return the device to the Unselected state: Perform a correct Operate Once request (8a) Perform a correct Operate Once request and force the output of the device such that the output keeps its old state (8b) Perform a correct Operate Once request and force the output of the device such that the output keeps reaches the 'between' state (8c) |
|  | Path 2+4+9a/b/c (returning to the Ready state): Select device correctly using SelectWithValue Send a correct Operate request Verify each of these paths will return the device to the Ready state: Perform a correct Operate Many request (9a) Perform a correct Operate Many request and force the output of the device such that the output keeps its old state (9b) Perform a correct Operate Many request and force the output of the device such that the output keeps reaches the 'between' state (9c) |
|  | Path 2+5+7+9a/b/c (returning to the Ready state): Select device correctly [SelectWithValue] Send a correct TimeActivatedOperate request After the timer has expired, test each of these paths which will return the device to the Ready State: Perform a correct Operate Many request (9a) Perform a correct Operate Many request and force the output of the device such that the output keeps its old state (9b) Perform a correct Operate Many request and force the output of the device such that the output keeps reaches the 'between' state (9c) |

Detailed test procedures for SBOes

| SBOes1 | Incorrect SelectWithValue | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6 and 20.8.4 |
| Expected result DUT sends SelectWithValue response- with AddCause “Select-failed” or “Not-supported” |
| Test description Client sends SelectWithValue request with incorrect access right by setting an incorrect originator category |
| Comment |

| SBOes2 | SelectWithValue followed by Cancel, timeout or Operate resulting in test not ok | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result DUT responds with Cancel response+ DUT sends nothing DUT sends TimeActivatedOperate response- with error “Test Not OK” DUT sends Operate response- with error “Operator Test Not OK” In all cases the control object returns to the “unselected” state |
| Test description Client sends correct SelectWithValue request followed by: Client sends correct Cancel request Or Client waits for timeout Or force EQUIPMENT SIMULATOR that the Client TimeActivatedOperate request results in “test not ok” Or force EQUIPMENT SIMULATOR that the Client Operate request results in “test not ok” |
| Comment |

| SBOes3 | SelectWithValue, operate once followed by new, old and in between state change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result DUT responds with SelectWithValue response+ DUT responds with Operate response+ DUT reports CommandTermination+ After timeout DUT reports CommandTermination- with error “Timeout Test Not OK” and AddCause “invalid position” or “Time-limit-over” After timeout DUT reports CommandTermination- with error “Timeout Test Not OK” and with AddCause “invalid position” In all cases the control object returns to the “unselected” state |
| Test description Client sends correct SelectWithValue request Client sends correct Operate once request followed by Force EQUIPMENT SIMULATOR to go to the new state Or force EQUIPMENT SIMULATOR to keep the old state Or force EQUIPMENT SIMULATOR to go to the in between state |
| Comment |

| SBOes4 | SelectWithValue, TimeActivatedOperate once followed by failed wait for action time or cancel | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result DUT responds with SelectWithValue response+ DUT responds with TimeActivatedOperate response+ After wait time DUT reports TimeActivatedOperate response-- with error “Timeout Test Not Ok” and AddCause “Blocked-by-interlocking” DUT responds with Cancel response+ In all cases the control object returns to the “unselected” state |
| Test description Client sends correct SelectWithValue request Client sends correct TimeActivatedOperate once request During wait for activation time force EQUIPMENT SIMULATOR to create an interlock resulting in wait for action time – test not ok Or Client sends correct Cancel request |
| Comment |

| SBOes5 | SelectWithValue, TimeActivatedOperate once followed by new, old and in between state change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result DUT responds with SelectWithValue response+ DUT responds with TimeActivatedOperate response+ After wait time DUT reports timer expired test ok DUT reports command termination+ After wait for change timeout DUT reports CommandTermination- with error “Timeout Test Not OK” and AddCause “Invalid position” or “Time-limit-over” 6. After wait for change timeout DUT reports CommandTermination- with error “Timeout Test Not OK” and AddCause “Invalid position” In all cases the control object returns to the “unselected” state |
| Test description Client sends correct SelectWithValue request Client sends correct TimeActivatedOperate request After wait time DUT reports/responds timer expired test ok, followed by Force EQUIPMENT SIMULATOR to go to the new state Or force EQUIPMENT SIMULATOR to keep the old state Or force EQUIPMENT SIMULATOR to go to the in between state |
| Comment |

| SBOes6 | SelectWithValue, Operate many followed by new, old and in between state change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result In all cases the control object returns to the “ready” state |
| Test description Repeat SBOes3, but set the control object sboClass to “operate-many” |
| Comment |

| SBOes7 | SelectWithValue, TimeActivatedOperate many followed by new, old and in between state change | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 17.3.3 IEC 61850-8-1 clause 20.6, 20.7 and 20.8 |
| Expected result In all cases the control object returns to the “ready” state |
| Test description Repeat SBOes5, but set the control object sboClass to “operate-many” |
| Comment |

## A4.11	Time and time synchronization

Abstract test cases

|  | Verify the DUT supports the SCSM time synchronisation |
| --- | --- |
|  | Check report/logging timestamp accuracy matches the documented timestamp quality of the server |
|  | Verify that when the device supports time zones and daylight saving the time stamp of events and disturbance files are UTC time |

|  | Verify that when time synchronisation communication lost is detected after a specified period |
| --- | --- |
|  | On synchronisation error, deviation beyond time stamp tolerance should be detected |

Detailed test procedures

| Tm1 | SCSM time synchronisation (SNTP) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result DUT accepts the new time DUT updates the event DUT sends GetDataValues response+ with new UTC time |
| Test description Test engineer changes the time in the TIME MASTER Force an event using the EQUIPMENT SIMULATOR Client requests GetDataValues of the event |
| Comment |

| Tm2 | Time stamp accuracy | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result The time stamp quality matches with the documented accuracy |
| Test description Repeat Tm1, and check the time stamp quality |
| Comment |

| Tm3 | Time zone and daylight saving | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result 1. The time stamp is still UTC time |
| Test description 1. Configure DUT with a Time zone and Repeat Tm1 |
| Comment |

| TmN1 | Lost time synchronisation | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result DUT detects the lost time synch DUT updates the event DUT sends GetDataValues response+ with time quality ClockNotSynchronized |
| Test description Test engineer disconnects the TIME MASTER and waits specified period Force an event using the EQUIPMENT SIMULATOR Client requests GetDataValues of the event |
| Comment |

| TmN2 | ClockFailure | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 18 and 5.5.3.7.3.3 IEC 61850-8-1 clause 21 PIXIT |
| Expected result DUT keeps the old time DUT updates the event DUT sends GetDataValues response+ with old time and time quality “ClockFailure” |
| Test description Test engineer controls the TIME MASTER to force a ClockFailure as specified in the PIXIT Force an event using the EQUIPMENT SIMULATOR Client requests GetDataValues of the event |
| Comment |

## A4.12	File transfer

Abstract test cases

|  | Request a GetServerDirectory(FILE) with correct parameters and verify the response (IEC 61850-7-2 clause 6.2.2) |
| --- | --- |
|  | For each responded file: request a GetFile with correct parameters and verify the response (IEC 61850-7-2 clause 20.2.1) request a GetFileAttributeValues with correct parameters and verify the response (IEC 61850-7-2 clause 20.2.4) request a DeleteFile with correct parameters and verify the response (IEC 61850-7-2 clause 20.2.3) |
|  | Verify the SetFile service with a small and large file and the maximum number of maximum sized file |
|  | Request a GetFile from several clients simultaneously if more than one client association will be supported |

| FtN1 | Request following file transfer services with an unknown file name and verify the appropriate response- service error GetFile (IEC 61850-7-2 clause 20.2.1) GetFileAttributeValues (IEC 61850-7-2 clause 20.2.4) DeleteFile (IEC 61850-7-2 clause 20.2.3) |
| --- | --- |

Detailed test procedures for File transfer

| Ft1 | GetServerDirectory(FILE) | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 6.2.2 IEC 61850-8-1 clause 23, Tissue #118, PIXIT |
| Expected result 1. DUT sends GetServerDirectory(FILE) response+ with a list of files and/or directories according to the PIXIT. If the Filename (for instance MMS FileSpecification) is not present in the FileDirectory.request, then the responding server shall return the filenames present in the root directory |
| Test description Client requests GetServerDirectory(FILE) and for each responded directory Client requests GetServerDirectory(FILE) |
| Comment |

| Ft2 | GetFile, GetFileAttributeValues, DeleteFile | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.1, 20.2.4, 20.2.3 IEC 61850-8-1 clause 23.2.1, 23.2.3, 23.2.4 PIXIT |
| Expected result DUT sends GetFile response+ and sends the contents of the file DUT sends GetFileAttributeValues response+ DUT sends DeleteFile response+ |
| Test description For each responded file: Client requests GetFile with correct parameters Client requests GetFileAttributeValues with correct parameters Client requests DeleteFile with correct parameters |
| Comment |

| Ft3 | SetFile | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.2 IEC 61850-8-1 clause 23.2.2 PIXIT |
| Expected result DUT sends SetFile response+ and requests GetFile DUT stores contents of file DUT stores files DUT stores all files |
| Test description Client requests SetFile with a small file Client sends contents of the file repeat step 1 and 2 with a large (maximum) size file repeat step 3 10 times with unique file names |
| Comment |

| Ft4 | Simultaneous GetFile from 2 clients | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.1 IEC 61850-8-1 clause 23.2.1 PIXIT |
| Expected result DUT sends GetFile response+ DUT sends GetFile response+ or response- "file busy" (PIXIT) |
| Test description Client1 requests GetFile Client2 requests GetFile of the same file while the first GetFile is still in progress |
| Comment |

| FtN1 | GetFile, GetFileAttributeValues, DeleteFile with unknown file name | ( Passed ( Failed ( Inconclusive |
| --- | --- | --- |
| IEC 61850-7-2 clause 20.2.1, 20.2.4, 20.2.3 IEC 61850-8-1 clause 23.2 PIXIT |
| Expected result a) DUT sends GetFile response- b1) DUT shall return MMS service error "file file-non-existent" b2) DUT shall return the files in the root directory c) DUT sends DeleteFile response- |
| Test description a) Client requests GetFile with unknown file b1) Client requests GetFileAttributeValues with unknown file b2) Client requests GetFileAttributeValues with no file parameter in the request c) Client requests DeleteFile with unknown file |
| Comment |

## A4.13	Combinations & free form testing

Abstract test cases

|  | Test if reporting and control services keep on responding as specified while requesting other services Combine server actions: Reporting, Logging, Goose subscribing/publishing, Time Sync with client request services enable reporting enable logging enable Goose publishing send Goose messages enable time synch enable other supported services that consumes processing time at server Start requests of all supported request and control services. As soon as one request is responded issue a new request. Continue this for 10 minutes request logical server, logical node and data GetDataValues-services request GetDataSetValues-services request GetxRCBValues-services request QueryLog-services request GetFile-services select and operate control objects |
| --- | --- |

Detailed test procedures

For free form testing a test lab can add extra test cases/procedures and propose these to the UCAIUG. The UCAIUG decides if and how to include the test case.

# Annex B		Detailed description of test results

This appendix contains detailed comments on test results, for instance when a defect is detected or to explain an inconclusive test result, including the actual message flow if appropriate.

<Test procedure identifier X>

<Additional extra information, e.g. a trace dump>

<Test procedure identifier Y>

<Additional extra information, e.g. a trace dump>

# Annex C		TICS template for Server

Introduction

This document provides a template for the tissues conformance statement. According to the UCA IUG QAP the tissue conformance statement is required to perform a conformance test and is referenced on the certificate.

This document is applicable for <device> with firmware version <version>.

Mandatory IntOp Tissues

During the October 2006 meeting IEC TC57 working group 10 decided that:

- green Tissues with the category “IntOp” are mandatory for IEC 61850 edition 1

- Tissues with the category “Ed.2” Tissues should not be implemented.

Below table gives an overview of the implemented IntOp Tissues.

| Part | Tissue Description Implemented Nr Y/na |
| --- | --- |
| 8-1 | 116 GetNameList with empty response? Y 165 Improper Error Response for GetDataSetValues Y 183 GetNameList error handling Y |
| 7-4 | None |
| 7-3 | 28 Definition of APC Y/na 54 Point def xVal, not cVal Y/na 55 Ineut = Ires ? Y/na 60 Services missing in tables Y/na 63 mag in CDC CMV Y/na 219 operTm in ACT Y/na 270 WYE and DEL rms values Y/na |
| 7-2 | 30 control parameter T Y/na 31 Typo na 32 Typo in syntax na 35 Typo Syntax Control time na 36 Syntax parameter DSet-Ref missing Y/na 37 Syntax GOOSE "T" type Y/na 39 Add DstAddr to GoCB Y/na 40 GOOSE Message “AppID” to “GoID” Y/na 41 GsCB “AppID” to “GsID” Y/na 42 SV timestamp: “EntryTime” to “TimeStamp" Y/na 43 Control "T" semantic Y/na 44 AddCause - Object not sel Y/na 45 Missing AddCauses (neg range) Y/na 46 Synchro check cancel Y/na 47 "." in LD Name? Y/na 49 BRCB TimeOfEntry (part of #453) - 50 LNName start with number? Y/na 51 ARRAY [0..num] missing Y/na 52 Ambiguity GOOSE SqNum Y/na 53 Add DstAddr to GsCB, SV Y/na 151 Name constraint for control blocks etc. Y/na 166 DataRef attribute in Log Y/na 185 Logging - Integrity periode Y/na 189 SV Format na 190 BRCB: EntryId and TimeOfEntry (part of #453) - 191 BRCB: Integrity and buffering reports (part of #453) - 234 New type CtxInt (Enums are mapped to 8 bit integer) Y/na 275 Confusing statement on GI usage (part of #453) - 278 EntryId not valid for a server (part of #453) - |
| Part 6 | 1 Syntax Y/na 5 tExtensionAttributeNameEnum is restricted Y/na 8 SIUnit enumeration for W Y/na 10 Base type for bitstring usage Y/na 17 DAI/SDI elements syntax Y/na 169 Ordering of enum differs from 7-3 Y/na |

NOTE:	Tissue 49, 190, 191, 275 and 278 are part of the optional tissue #453, all other technical tissues in the table are mandatory if applicable.

NOTE: 	Editorial tissues are marked as “na”.

NOTE: 	Final proposal on tissue 45 is not defined yet

Optional IntOp Tissues

After the approval of the server conformance test procedures version 2.2 the following IntOp tissues were added or changed. It is optional to implement these tissues.

| Part | Tissue Nr | Description | Implemented Y/N/na |
| --- | --- | --- | --- |
| 8-1 | 246 | Control negative response (SBOns) with LastApplError | Y/N/na |
| 8-1 | 545 | Skip file directories with no files | Y/N/na |
| 7-2 | 333 | Enabling of an incomplete GoCB | Y/N/na |
| 7-2 | 453 | Combination of all reporting and logging tissues | Y/N/na |
| 6 | 245 | Attribute RptId in SCL is optional | Y/N/na |
| 6 | 529 | Replace sev - Unknown by unknown | Y/N/na |

Other Implemented Tissues

<Complete below table of other implemented tissues, these tissues should have no impact on interoperability>

| Part | Tissue Nr | Description |
| --- | --- | --- |

Instruction and comments on using this template

Comments

- Tissue 235 “Extension of name length” for datset references has been changed from IntOp to Ed.2 and has been removed from the IntOp list, Tissue 235 shall not be implemented for Ed1 devices

- Tissue 38 “Change AppId into GoId" to match part 7-2 with part 8-1 has been changed from IntOp to Ed.2 and has been removed from the IntOp list

- Tissue 45 “Additional AddCauses" has been changed from green to red

- Tissue 65 category has been changed from IntOp to Ed2

- Even intop tissues may change. Compare http://www.tissues.iec61850.com for most recent status

- Questions and comments can be e-mailed to: helpdesk@ucausersgroup.org

Instructions

- format of the document may be changed into your company format

- enter the applicable IED name and firmware version

- update the Y/na values in the Mandatory tissue table

- update the Y/N/na values in the Optional tissue table

- remove the instructions, comments and revision history of the template

Revision history

| Revision | Remarks |
| --- | --- |
| 0.1 | First version of the UCAIUG template |
| 0.2 (okt 2008) | Removed tissue 38 from the list Added a note on tissue 45 |
| 0.3 (okt 2010) | Tissue 65 category has been changed from IntOp to Ed2. Removed tissue 65 from the IntOp list |
| Version 2.3 | Included in the test procedures document, |

# Annex D		PIXIT template for Server

Introduction

This document specifies the protocol implementation extra information for testing (PIXIT) of the IEC 61850 interface in <device> with firmware version <version>.

Together with the PICS and the MICS the PIXIT forms the basis for a conformance test according to IEC 61850-10.

Contents of this document

Each chapter specifies the PIXIT for each applicable ACSI service model as structured in IEC 61850-10.

PIXIT for Association model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| As1 | Maximum number of clients that can set-up an association simultaneously | … |
| As2 | TCP_KEEPALIVE value | … seconds |
| As3 | Lost connection detection time | … seconds |
| As4 | Is authentication supported | Y/N |
| As5 | What association parameters are necessary for successful association | Transport selector Y/N Session selector Y/N Presentation selector Y/N AP Title Y/N AE Qualifier Y/N |
| As6 | If association parameters are necessary for association, describe the correct values e.g. | Transport selector 0001 Session selector 0001 Presentation selector 00000001 AP Title <value> AE Qualifier <value> |
| As7 | What is the maximum and minimum MMS PDU size | Max MMS PDU size … Min MMS PDU size … |
| As8 | What is the maximum start up time after a power supply interrupt | … seconds |
|  | <additional items> |  |

PIXIT for Server model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Sr1 | Which analogue value (MX) quality bits are supported (can be set by server) | Validity: Y/N Good, Y/N Invalid, Y/N Reserved, Y/N Questionable Y/N Overflow Y/N OutofRange Y/N BadReference Y/N Oscillatory Y/N Failure Y/N OldData Y/N Inconsistent Y/N Inaccurate Source: Y/N Process Y/N Substituted Y/N Test Y/N OperatorBlocked |
| Sr2 | Which status value (ST) quality bits are supported (can be set by server) | Validity: Y/N Good, Y/N Invalid, Y/N Reserved, Y/N Questionable Y/N BadReference Y/N Oscillatory Y/N Failure Y/N OldData Y/N Inconsistent Y/N Inaccurate Source: Y/N Process Y/N Substituted Y/N Test Y/N OperatorBlocked |
| Sr3 | What is the maximum number of data values in one GetDataValues request |  |
| Sr4 | What is the maximum number of data values in one SetDataValues request |  |
| Sr5 | Which Mode / Behaviour values are supported | On Y/N Blocked Y/N Test Y/N Test/Blocked Y/N Off Y/N |
|  | <additional items> |  |

PIXIT for Data set model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Ds1 | What is the maximum number of data elements in one data set (compare ICD setting) |  |
| Ds2 | How many persistent data sets can be created by one or more clients |  |
| Ds3 | How many non-persistent data sets can be created by one or more clients |  |
|  | <additional items> |  |

PIXIT for Substitution model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Sb1 | Are substituted values stored in volatile memory? | Y/N |
|  | <additional items> |  |

PIXIT for Setting group control model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Sg1 | What is the number of supported setting groups for each logical device (compare NumSG in the SGCB) |  |
| Sg2 | What is the effect of when and how the non-volatile storage is updated (compare IEC 61850-8-1 $16.2.4) |  |
| Sg3 | Can multiple clients edit the same setting group | Y/N |
| Sg4 | What happens if the association is lost while editing a setting group | Y/N |
| Sg5 | Is EditSG value 0 allowed? | Y/N |
|  | <additional items> |  |

PIXIT for Reporting model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Rp1 | The supported trigger conditions are (compare PICS) | integrity Y/N data change Y/N quality change Y/N data update Y/N general interrogation Y/N |
| Rp2 | The supported optional fields are | sequence-number Y/N report-time-stamp Y/N reason-for-inclusion Y/N data-set-name Y/N data-reference Y/N buffer-overflow Y/N entryID Y/N conf-rev Y/N segmentation Y/N |
| Rp3 | Can the server send segmented reports | Y/N |
| Rp4 | Mechanism on second internal data change notification of the same analogue data value within buffer period (Compare IEC 61850-7-2 $14.2.2.9) | Send report immediately OR Replace analogue value in pending report |
| Rp5 | Multi client URCB approach (compare IEC 61850-7-2 $14.2.1) | Each URCB is visible to one client only or Each URCB is visible to all clients |
| Rp6 | What is the format of EntryID |  |
| Rp7 | What is the buffer size for each BRCB or how many reports can be buffered |  |
| Rp8 | Pre-configured RCB attributes that cannot be changed online when RptEna = FALSE (see also the ICD report settings) |  |
| Rp9 | May the reported data set contain: - structured data objects? - data attributes? | Y/N Y/N |
| Rp10 | What is the scan cycle for binary events? Is this fixed, configurable | …. Mseconds Fixed or Configurable |
| Rp11 | Does the device support to pre-assign a RCB to a specific client in the SCL | Y/N |
|  | <additional items> |  |

PIXIT for Logging model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Lg1 | What is the default value of LogEna (Compare IEC 61850-8-1 $17.3.3.2.1, the default value should be FALSE) | TRUE/FALSE |
| Lg2 | What is the format of EntryID (Compare IEC 61850-8-1 $17.3.3.3.1) |  |
| Lg3 | If there are multiple Log Control Blocks that specify the Journaling of the same MMS NamedVariable and TrgOps and the Event Condition (Compare IEC 61850-8-1 $17.3.3.3.2) | Single Journal Entry (specify the event condition) or Multiple Journal Entries |
| Lg4 | Pre-configured LCB attributes that cannot be changed online |  |
|  | <additional items> |  |

PIXIT for Generic substation events model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Go1 | What elements of a subscribed GOOSE header are checked to decide the message is valid and the allData values are accepted? If yes, describe the conditions. Note: the VLAN tag may be removed by a ethernet switch and should not be checked | Y/N source MAC address Y/N destination MAC address Y Ethertype = 0x88B8 Y/N APPID Y/N gocbRef Y/N timeAllowedtoLive Y/N datSet Y/N goID Y/N t Y/N stNum Y/N sqNum Y/N test Y/N confRev Y/N NdsCom Y/N numDatSetEntries |
| Go2 | Can the test flag in the published GOOSE be turned on / off | Y/N |
| Go3 | What is the behaviour when the GOOSE publish configuration is incorrect | DUT will send GOOSE with NdsCom=T or DUT keeps GoEna=F |
| Go4 | When is a subscribed GOOSE marked as lost? (TAL = time allowed to live value from the last received GOOSE message) | a) message does not arrive prior to TAL b) message does not arrive by 2x TAL c) message does not arrive by TAL plus configurable time d) other (describe) |
| Go5 | What is the behaviour when one or more subscribed GOOSE messages isn’t received or syntactically incorrect (missing GOOSE) |  |
| Go6 | What is the behaviour when a subscribed GOOSE message is out-of-order |  |
| Go7 | What is the behaviour when a subscribed GOOSE message is duplicated |  |
| Go8 | Does the device subscribe to GOOSE messages with/without the VLAN tag? | Y/N, with the VLAN tag Y/N, without the VLAN tag |
| Go9 | May the GOOSE data set contain: - structured data objects (FCD)? - timestamp data attributes? Note: data attributes (FCDA) is mandatory | Subscribed Published Y/N Y/N Y/N Y/N |
| Go10 | Published FCD supported common data classes are | <list of common data classes> |
| Go11 | Subscribed FCD supported common data classes are | <list of common data classes> |
| Go12 | What is the slow retransmission time? Is it fixed or configurable? | … mseconds with TAL = … Fixed or Configured by …. |
| Go13 | What is the fast retransmission scheme? Is it fixed or configurable? | 1) … mseconds with TAL = … 2) … mseconds with TAL = … 3) … mseconds with TAL = … 4) … mseconds with TAL = … 5) … mseconds with TAL = … 6) … mseconds with TAL = … Fixed or Configured by …. |
| Go14 | Can the Goose publish be turned on / off by using SetGoCBValues(GoEna) | Y/N |
|  | <additional items> |  |

TAL = Time Allowed to Live

PIXIT for Control model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Ct1 | What control models are supported (compare PICS) | Y/N status-only Y/N direct-with-normal-security Y/N sbo-with-normal-security Y/N direct-with-enhanced-security Y/N sbo-with-enhanced-security |
| Ct2 | Is the control model fixed, configurable and/or online changeable? | Fixed / Configurable / Online changeable |
| Ct3 | Is TimeActivatedOperate supported | Y/N |
| Ct4 | Is “operate-many” supported | Y/N |
| Ct5 | Will the DUT activate the control output when the test attribute is set in the SelectWithValue and/or Operate request (when N test procedure Ctl2 is applicable) | Y/N |
| Ct6 | What are the conditions for the time (T) attribute in the SelectWithValue and/or Operate request | e.g. DUT ignores the time value and execute the command as usual |
| Ct7 | Is pulse configuration supported | Y/N |
| Ct8 | What is the behaviour of the DUT when the check conditions are set Is this behaviour fixed, configurable, online changeable? | Y/N synchrocheck Y/N interlock-check DUT ignores the check value and always perform the check or DUT uses the check value to perform the check Fixed / Configurable / Online changeable |
| Ct9 | What additional cause diagnosis are supported | Y/N Blocked-by-switching-hierarchy Y/N Select-failed Y/N Invalid-position Y/N Position-reached Y/N Parameter-change-in-execution Y/N Step-limit Y/N Blocked-by-Mode Y/N Blocked-by-process Y/N Blocked-by-interlocking Y/N Blocked-by-synchrocheck Y/N Command-already-in-execution Y/N Blocked-by-health Y/N 1-of-n-control Y/N Abortion-by-cancel Y/N Time-limit-over Y/N Abortion-by-trip |
| Ct10 | How to force a “test-not-ok” respond with SelectWithValue request? |  |
| Ct11 | How to force a “test-not-ok” respond with Select request? |  |
| Ct12 | How to force a “test-not-ok” respond with Operate request? | DOns: SBOns: DOes: SBOes: |
| Ct13 | Which origin categories are supported? |  |
| Ct14 | What happens if the orCat value is not supported? | DOns: SBOns: DOes: SBOes: |
| Ct15 | Does the IED accept a SelectWithValue/Operate with the same ctlVal as the current status value? | DOns: Y/N SBOns: Y/N DOes: Y/N SBOes: Y/N |
| Ct16 | Does the IED accept a select/operate on the same control object from 2 different clients at the same time? | DOns: Y/N (default Y) SBOns: Y/N (default N) DOes: Y/N (default Y) SBOes: Y/N (default N) |
| Ct17 | Does the IED accept a Select/SelectWithValue from the same client when the control object is already selected (tissue 334) | SBOns: Y/N SBOes: Y/N |
| Ct18 | Is for SBOes the internal validation performed during the SelectWithValue and/or Operate step? | SelectWithValue / Operate / SelectWithValue and Operate |
| Ct19 | Can a control operation be blocked by Mod=Off or Blocked | Y/N |
| Ct20 | Does the IED support local / remote operation? | Y/N |
| Ct21 | Does the IED send an InformationReport with LastApplError as part of the Operate response- for control with normal security? | SBOns: Y/N DOns: Y/N |
|  | <additional items> |  |

PIXIT for Time and time synchronisation model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Tm1 | What quality bits are supported (may be set by the IED) | Y/N LeapSecondsKnown Y/N ClockFailure Y/N ClockNotSynchronized |
| Tm2 | Describe the behaviour when the time synchronization signal/messages are lost |  |
| Tm3 | When is the time quality bit "ClockFailure" set? |  |
| Tm4 | When is the time quality bit "Clock not synchronised” set? |  |
| Tm5 | Is the timestamp of a binary event adjusted to the configured scan cycle? | Y/N |
| Tm6 | Does the device support time zone and daylight saving? | Y/N |
| Tm7 | Which attributes of the SNTP response packet are validated? | Y/N Leap indicator not equal to 3? Y/N Mode is equal to SERVER Y/N OriginateTimestamp is equal to value sent by the SNTP client as Transmit Timestamp Y/N RX/TX timestamp fields are checked for reasonableness Y/N SNTP version 3 and/or 4 Y/N other (describe) |
|  | <additional items> |  |

PIXIT for File transfer model

| ID | Description | Value / Clarification |
| --- | --- | --- |
| Ft1 | What is structure of files and directories? |  |
| Ft2 | Directory names are separated from the file name by | “/” or “\” |
| Ft3 | The maximum file name size including path (recommended 64 chars) | … chars |
| Ft4 | Are directory/file name case sensitive | Case sensitive |
| Ft5 | Maximum file size |  |
| Ft6 | Is the requested file path included in the MMS fileDirectory respond file name? | Y/N |
| Ft7 | Is the wild char supported MMS fileDirectory request? | Yes, wild card = * No |
| Ft8 | Is it allowed that 2 clients get a file at the same time? | Y/N |
|  | <additional items> |  |

Instruction and comments on using the PIXIT template

Comments

- The template is updated according to the PIXIT references in the server conformance test procedures version 2.3

- Questions and comments can be e-mailed to: helpdesk@ucausersgroup.org

Instructions

- format of the document may be changed into your company format

- enter the applicable IED name and firmware version

- remove the non-applicable clauses

- remove the <additional items> row

- add new rows when/where applicable to describe additional functionality important for testing

PIXIT Revision history

| Revision | Remarks |
| --- | --- |
| 1.1 draft | Added default values for the control entries related to CtlN4 and CtlN8 test cases |
|  | Added APPID to first GOOSE entry |
| Version 2.3 | Included into server test procedures version 2.3, Added IDs for easier referencing and PIXIT review, added Ct21; Added GOOSE supported FCD entries |

# Annex E		Server Certificate Template

# Comments

Does this need to be changed to refer to the PIXIT?

Fix this and a, b,c
make the sending of NdsComm conditional on the PIXIT.

# Text boxes

Utrechtseweg 310, 6812 AR Arnhem, the Netherlands.

Telephone +31 26 3 56 91 11. Telefax + 31 26 3 51 56 06.

Copyright © KEMA Nederland B.V., Arnhem, the Netherlands. All rights reserved.

This document  may be distributed to UCA international users group members only.

KEMA Nederland B.V. and/or its associated companies disclaim liability for any direct, indirect, consequential or incidental damages that may result from the use of the information or data, or from the inability to use the information or data.

EQUIPMENT SIMULATOR

Ethernet switching Hub

SIMULATOR

ANALYZER

Device Under

Test (DUT)

Time Master

| IEC 61850 Certificate Level A/B1 | No. << certificate number>> |
| --- | --- |
| Issued to: | For the product: |
| <<TEST INITIATOR>> <<FULL ADDRESS>> | <<PRODUCT NAME>> <<VERSION NUMBER>> <<ADDITIONAL INFO>> |

Issued by: <<test tlab>>

# The product has not shown to be non-conforming to:

IEC 61850-6, 7-1, 7-2, 7-3, 7-4 and 8-1

Communication networks and systems in substations

The conformance test has been performed according to IEC 61850-10 with product’s protocol, model and technical issue implementation conformance statements: “<<PICS>>”, “<<MICS>>”, “<<TICS>>” and product’s extra information for testing: “<<PIXIT>>”.

The following IEC 61850 conformance blocks have been tested with a positive result (number of relevant and executed test cases / total number of test cases as defined in the UCA International Users Group Device Test procedures v2.3 with TPCL version 1.2):

| 1 Basic Exchange (../24) 2 Data Sets (../6) 2+ Data Set Definition (../23) 3 Substitution (../4) 4 Setting Group Selection (../3) 4+ Setting Group Definition (7/7) 5 Unbuffered Reporting (../19) 6 Buffered Reporting (../21) | 9a GOOSE Publish (../13) 9b GOOSE Subscribe (../11) 12a Direct Control (../12) 12b SBO Control (../14) 12c Enhanced Direct Control (../13) 12d Enhanced SBO Control (../19) 13 Time Synchronization (../5) 14 File Transfer (../7) |
| --- | --- |

This Certificate includes a summary of the test results as carried out at <<CITY>> in <<COUNTRY>> with <<CLIENT SIMULATOR> <<VERSION>> with test suite <<VERSION>> and <<ANALYZER>> <<VERSION>>. The test is based on the UCA International Users Group Device Test Procedures version 2.3. This document has been issued for information purposes only, and the original paper copy of the <<TESTLAB>> report: No. <<TESTREPORT NUMBER>> will prevail.

The test has been carried out on one single specimen of the product as referred above and submitted to <<TESTLAB>> by <<TEST INITIATOR>>. The  manufacturer’s production process has not been assessed. This certificate does not imply that <<TESTLAB>> has certified or approved any product other than the specimen tested.

<<CITY>>, <<DATE>>

<<Manager NAME>>	<<Tester NAME>>

<<JOB TITLE>>	<<JOB TITLE>>

# 1 Level A - Independent Test lab with certified ISO 9000 or ISO 17025 Quality System

Applicable Test Procedures from the UCA International Users Group Device Test Procedures version 2.3

| Conformance Block | Mandatory | Conditional |
| --- | --- | --- |
| 1: Basic Exchange | Ass1, Ass2, Ass3, AssN2, AssN3, AssN4, AssN5 Srv1, Srv2, Srv3, Srv4, Srv5, SrvN1abcd, SrvN4 | AssN6 Srv6, Srv7, Srv8, Srv9, Srv10, SrvN1e, SrvN1f, SrvN2, SrvN3 |
| 2: Data Sets | Dset1, Dset10a, DsetN1ae | Dset10b, DsetN1b, DsetN16 |
| 2+: Data Set Definition | Dset2, Dset3, Dset4, Dset5, Dset6, Dset7, Dset8, Dset9 DsetN1cd, DsetN2, DsetN3, DsetN4, DsetN5, DsetN6, DsetN7, DsetN8, DsetN9, DsetN10, DsetN11, DsetN12, DsetN13, DsetN14, DsetN15 |  |
| 3: Substitution | Sub1, Sub2, Sub3, SubN1 |  |
| 4: Setting Group Selection | Sg1, SgN1a | Sg3 |
| 4+: Setting Group Definition | Sg2, Sg4, SgN1b, SgN2, SgN3, SgN4, SgN5 |  |
| 5: Unbuffered Reporting | Rp1, Rp2, Rp3, Rp4, Rp7, Rp10, Rp12 RpN1, RpN2, RpN3, RpN4 | Rp5, Rp6, Rp8, Rp9, Rp11, RpN5, RpN6, RpN7 |
| 6: Buffered Reporting | Br1, Br2, Br3, Br4, Br7, Br8, Br9, Br12, Br14 BrN1, BrN2, BrN3, BrN4, BrN5 | Br5, Br6, Br10, Br11, Br13, BrN6, BrN7 |
| 6+: Enhanced buffered reporting | BrE1, BrE2, BrE3, BrE6, BrE7, BrE8, BrE9, BrE10, BrE11 | BrE4, BrE5, BrE12 |
| 9a: GOOSE publish | Gop2, Gop3, Gop4, Gop7a, Gop9a, Gop10a | Gop1, Gop5, Gop6, Gop8, Gop7b, Gop9b, Gop10b, GopN1, GopN2 |
| 9b: GOOSE subscribe | Gos1a, Gos2, Gos3, GosN1, GosN2, GosN3, GosN4, GosN5, GosN6 | Gos1b, Gos4 |
| 12a: Direct control | CtlN3, CtlN8 DOns1, DOns3 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 DOns2, DOns4, DOns5 |
| 12b: SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, SBOns2 | Ctl2, Ctl4, Ctl7, CtlN10, CtlN11 SBOns3, SBOns4, SBOns5 |
| 12c: Enhanced Direct Control | CtlN3, CtlN8 DOes2, DOes5 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11 DOes1, DOes3, DOes4 |
| 12d: Enhanced SBO control | Ctl3, CtlN1, CtlN2, CtlN3, CtlN4, CtlN9 SBOes1, SBOes2, SBOes3 | Ctl2, Ctl4, Ctl7, CtlN6, CtlN10, CtlN11 SBOes4, SBOes5, SBOes6, SBOes7 |
| 13: Time sync | Tm1, Tm2, TmN1 | Tm3, TmN2 |
| 14: File transfer | Ft1, Ft2ab, Ft4, FtN1ab | Ft2c, Ft3, FtN1c |

[ All configuration file and data model tests have been successfully performed for the product variants using the same hardware and software version: <<Variant2>>, <<Variant3>> ]